DRAFT WHITE PAPER

Technical Requirements for Load Resources Providing Non-Spin

- Describe ERCOT criteria used for baseline qualification

  - ERCOT may qualify the LR for one or more of its default baseline methodologies used for ERS performance evaluation.

- Validation of baselines created via SPC+2 telemetry data

  - ERCOT will archive the telemetry data points received from the LR and will periodically compare those values to the LR’s aggregated 15-minute meter data

  - Define process for exclusion of days with LR deployments unrelated to ERCOT Ancillary Services

  - Define acceptable bandwidth/tolerance

    - Percentage basis

  - SPC+2 validation accommodating errors in Load forecast

    - Pull data for the mid-term Load forecast by weather zone

    - ERCOT MTLF MAPE subtracted from value determined in (c) above

    - QSE error may be no greater than X% of MTLF MAPE (X >= 100%)

    - Failure to meet acceptable bandwidth/tolerance:

      - ERCOT shall derate demand response value which will affect LRNEDP scores as well as QSE payment.  Subject to restoration after additional SPC+2 validation.

      - Any deration shall be noted in the LRNEDP report

  - On Nonspin deployment days, ERCOT will compute demand response value using an ERCOT-calculated baseline and compare to demand response value from SPC+2.

- ERCOT will re-validate baselines periodically and may revoke the baseline qualification based on a periodic analysis.

  - Applies to all validations described in (2) above.

- Obligation of LR across a Nonspin deployment

  - LR must perform consistent with awarded obligation or QSE must replace any short capacity (captured in LRNEDP calculation)

- Return to Service requirements

  - Must be restored to a state ready to meet Non-spin obligations within three hours of recall, unless no longer obligated at that time