| NPRR Number | 524 | NPRR Title | Resource Limits in Providing Ancillary Service |
| --- | --- | --- | --- |
| Date |  | March 20, 2013 |  |
| Submitter’s Information |  |  |  |
| Name |  | Bill Blevins / Sandip Sharma |  |
| E-mail Address |  | bblevins@ercot.com / ssharma@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-6691 / 512-248-4298 |  |
| Cell Number |  | 512-912-6314 / 817-371-7773 |  |
| Market Segment |  | Not applicable |  |

Comments

ERCOT files these comments to highlight its concern with this Nodal Protocol Revision Request (NPRR) and clarify that Responsive Reserve (RRS) Service must be frequency responsive and must respond to arrest frequency decay within the first few seconds.  RRS is a reliability tool and ERCOT uses RRS to arrest frequency decay triggered by sudden Forced Outages of Generation Resources.

In August 2012, the Performance, Disturbance, Compliance Working Group (PDCWG) produced a report that was based on a particular North American Electric Reliability Corporation (NERC) Disturbance Control Standard (DCS) event.  In that report PDCWG identified that there was high risk of ERCOT failing a DCS.  Specifically PDCWG identified that ”[i]f the ERCOT system has exhausted all available capacity and depended only on PFR and the subsequent energy deployed from RRS providers, ERCOT would fail the DCS standard.”

In September 2012, PDCWG made another report in which the group agreed that RRS capacity should not be carried on power augmentation that is not frequency responsive.

The currently proposed NPRR would allow RRS to be provided by Resources that are not able to provide Primary Frequency Response.  This would exacerbate the problem identified in the PDCWG reports and further degrade ERCOT response to disturbances.  The proposed NPRR would create less Primary Frequency Response during periods where the ERCOT System has exhausted all available capacity, which would result in more frequent tripping of Load Resources and higher potential for under-frequency Load shed.

ERCOT is opposed to the additional language as proposed in Section 3.18, Resource Limits in Providing Ancillary Service, and is providing these comments to clarify that RRS capacity should be fully frequency responsive.  ERCOT is recommending that the term “Frequency Responsive” be defined and inserted in Section 3.18 as a clarification.

ERCOT supports the proposed change to require telemetry for the portion of Resource  capacity that is available but is not Frequency Responsive.  This requirement would help ERCOT analyze grid disturbances and better determine system needs, so ERCOT is recommending that any such capacity be calculated by the Resource and sent to ERCOT as operational data.  However, ERCOT is recommending this telemetry requirement, which was proposed by the original NPRR524 submission, be included instead in Section 6.5.5.2, Operational Data Requirements.

Revised Cover Page Language

| Nodal Protocol Sections Requiring Revision | 2.1, Definitions 3.18, Resource Limits in Providing Ancillary Service 6.5.5.2, Operational Data Requirements |
| --- | --- |
| Revision Description | This Nodal Protocol Revision Request (NPRR) will clarify that Responsive Reserve (RRS) service capacity must always be Frequency Responsive (i.e., able to respond to arrest frequency decay within the first few seconds of a significant frequency deviation on the ERCOT Transmission Grid using Primary Frequency Response and interruptible Load). This NPRR also requires that the portion of Resource capacity that is available but is not Frequency Responsive be sent to ERCOT via Inter-Control Center Communications Protocol (ICCP) telemetry. |
| Reason for Revision | In August 2012, the Performance, Disturbance, Compliance Working Group (PDCWG) produced a report that was based on a particular North American Electric Reliability Corporation (NERC) Disturbance Control Standard (DCS) event. In that report PDCWG identified that there was high risk of ERCOT failing a DCS. Specifically PDCWG identified that ”[i]f the ERCOT system has exhausted all available capacity and depended only on PFR and the subsequent energy deployed from RRS providers, ERCOT would fail the DCS standard.” PDCWG also recommended in a September 2012 report that RRS capacity should not be carried on power augmentation that is not Frequency Responsive. To address these concerns, this NPRR clarifies that all RRS capacity must be Frequency Responsive. |

Revised Proposed Protocol Language

2.1	DEFINITIONS

Frequency Responsive

Able to respond to arrest frequency decay within the first few seconds of a significant frequency deviation on the ERCOT Transmission Grid using Primary Frequency Response and interruptible Load.

3.18	Resource Limits in Providing Ancillary Service

(1)	For both Generation Resources and Load Resources the High Sustained Limit (HSL) must be greater than or equal to the Low Sustained Limit (LSL) and the sum of the Resource-specific designation of capacity to provide Responsive Reserve (RRS), Regulation Up (Reg-Up), Regulation Down (Reg-Down), and Non-Spinning Reserve (Non-Spin).

(2)	For Non-Spin, the amount of Non-Spin provided must be less than or equal to the HSL for Off-Line Generation Resources.

(3)	For RRS Service:

(a)	The full amount of RRS provided from a Generation Resource must be less than or equal to 24% of thermal unit HSL for an Ancillary Service Offer, must be less than or equal to ten times the Emergency Ramp Rate, and must be Frequency Responsive;

(b)	Hydro Generation Resources operating in the synchronous condenser fast-response mode may provide RRS up to the hydro Generation Resource’s proven 20-second response capability (which may be 100% of the HSL).  The initiation setting of the automatic under-frequency relay setting shall not be lower than 59.80 Hz;

(c)	For any hydro Generation Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 24% of the HSL; and

(d)	The amount of RRS provided from a Load Resource must be less than or equal to the HSL minus the sum of the LSL, Reg-Up Resource Responsibility, Reg-Down Resource Responsibility, and Non-Spin Resource Responsibility.

6.5.5.2	Operational Data Requirements

(1)	ERCOT shall use Operating Period data to monitor and control the reliability of the ERCOT Transmission Grid and shall use it in network analysis software to predict the short-term reliability of the ERCOT Transmission Grid.  Each TSP, at its own expense, may obtain that Operating Period data from ERCOT or directly from QSEs.

(2)	A QSE representing a Generation Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time telemetry data to ERCOT for each Generation Resource.  ERCOT shall make that data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to requesting TSPs and DSPs operating within ERCOT.  Such data must be provided to the requesting TSP or DSP at the requesting TSP’s or DSP’s expense, including:

(a)	Net real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered gross real power and conversion constants determined by the Resource Entity and provided to ERCOT as a result of Section 3.7, Resource Parameters.  Net real power represents the actual generation of a Resource for all real power dispatch purposes, including use in Security-Constrained Economic Dispatch (SCED), determination of the High Ancillary Service Limit (HASL), High Dispatch Limit (HDL), Low Dispatch Limit (LDL) and Low Ancillary Service Limit (LASL), and is consistent with telemetered HSL and LSL;

(b)	Gross real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered real power, which may include Supervisory Control and Data Acquisition (SCADA) metering, and conversions constants determined by the Resource Entity and provided to ERCOT as a result of Section 3.7;

(c)	Gross Reactive Power (in Megavolt-Amperes reactive (MVAr));

(d)	Net Reactive Power (in MVAr);

(e)	Power to standby transformers serving plant auxiliary Load;

(f)	Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid;

(g)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(h)	Generation Resource breaker and switch status;

(i)	HSL;

(j)	High Emergency Limit (HEL), under Section 6.5.9.2, Failure of the SCED Process;

(k)	Low Emergency Limit (LEL), under Section 6.5.9.2;

(l)	LSL;

(m)	Configuration identification for Combined Cycle Generation Resources;

(n)	Ancillary Service Schedule for each quantity of RRS and Non-Spin which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment;

(o)	Ancillary Service Resource Responsibility for each quantity of Regulation Up (Reg-Up), Regulation Down (Reg-Down), RRS and Non-Spin.  The sum of Ancillary Service Resource Responsibility for all Resources in a QSE is equal to the Ancillary Service Supply Responsibility for that QSE; and

(p)	Reg-Up and Reg-Down Services participation factors represent how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s).

(q)	The designated Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources shall provide Real-Time telemetry for items (a), (b), (c), (d), (e), (g), and (h) above, PSS and AVR status for the total Generation Resource in addition to the Split Generation Resource the Master QSE represents.

(r)	If a Generation Resource’s telemetered HSL includes supplemental capacity that is not Frequency Responsive, a MW value reflecting the portion of the Generation Resource capacity that is not Frequency Responsive must be provided to ERCOT by Inter-Control Center Communications Protocol (ICCP) telemetry.

(3)	For each Wind-powered Generation Resource (WGR), the QSE shall set the HSL equal to the current net output capability of the facility.  The net output capability should consider the net real power of the WGR, turbine availability, weather conditions, and whether the WGR net output is being affected by compliance with a SCED Dispatch Instruction.

(4)	For each Aggregate Generation Resource (AGR), the QSE shall telemeter the number of its generators online.

(5)	A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP’s or DSP’s expense.  The Load Resource’s net real power consumption, Low Power Consumption (LPC) and Maximum Power Consumption (MPC) shall be telemetered to ERCOT using a positive (+) sign convention:

(a)	Load Resource net real power consumption (in MW);

(b)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(c)	Load Resource breaker status;

(d)	LPC (in MW);

(e)	MPC (in MW);

(f)	Ancillary Service Schedule (in MW) for each quantity of RRS and Non-Spin;

(g)	Ancillary Service Resource Responsibility (in MW) for each quantity of Reg-Up and Reg-Down for Controllable Load Resources, and RRS and Non-Spin for all Load Resources;

(h)	The status of the high-set under-frequency relay, if required for qualification;

(i)	For a Controllable Load Resource, the Scheduled Power Consumption that represents zero Ancillary Service deployments;

(j)	For a Controllable Load Resource, net Reactive Power (in MVAr);

(k)	Resource Status (Resource Status shall be ONRL if high-set under-frequency relay is active); and

(l)	Reg-Up and Reg-Down services participation factor, which represents how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource.

(6)	A QSE with Resources used in SCED shall provide communications equipment to receive ERCOT-telemetered control deployments.

(7)	A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-Down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE.  This temporary blocking will be indicated by the enabling of the Raise Block Status and/or Lower Block Status telemetry points.

(a)	Raise Block Status and Lower Block Status are telemetry points used in transient unit conditions to communicate to ERCOT that a Resource’s ability to adjust its output has been unexpectedly impaired.

(b)	When one or both of the telemetry points are enabled for a Resource, ERCOT will cease using the regulation capacity assigned to that Resource for Ancillary Service deployment.

(c)	This hiatus of deployment will not excuse the Resource’s obligation to provide the Ancillary Services for which it has been committed.

(d)	These telemetry points shall only be utilized during unforeseen transient unit conditions such as plant equipment failures.  Raise Block Status and Lower Block Status shall only be enabled until the Resource operator has time to update the Resource limits and Ancillary Service telemetry to reflect the problem.

(e)	The Resource limits and Ancillary Service telemetry shall be updated as soon as practicable.  Raise Block Status and Lower Block Status will then be disabled.

(8)	Real-Time data for reliability purposes must be accurate to within three percent.  This telemetry may be provided from relaying accuracy instrumentation transformers.

(9)	Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT.  The telemetered Resource Status for a Combined Cycle Generation Resource may only be assigned a Resource Status of OFFNS if no generation units within that Combined Cycle Generation Resource are On-Line.

(10)	A QSE representing combined-cycle Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits.  Combined Cycle Train power augmentation methods may only be included as part of one or more of the registered Combined Cycle Generation Resource configurations.  The Energy Offer Curve in the Three-Part Supply Offer that includes the offered power augmentation method may reflect the price of the added capability.  Such power augmentation methods may include:

(a)	Combustion turbine inlet air cooling (CTIAC) methods;

(b)	Duct firing;

(c)	Other ways of temporarily increasing the output of combined-cycle Resources; and

(d)	For Qualifying Facilities (QFs), an LSL that represents the minimum energy available, in MW, from the Combined Cycle Generation Resource for economic dispatch based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions.