## Slide 1: BSWG
Definition of “intended function”
ROS
April 11, 2013

## Slide 2: NERC EOP-005-2 R6
R6. Each Transmission Operator shall verify through analysis of actual events, steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed every five years at a minimum. Such analysis, simulations or testing shall verify: [Time Horizon = Long-term Planning]
R6.1. The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads.
R6.2. The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits.
R6.3. The capability of generating resources required to control voltages and frequency within acceptable operating limits.

## Slide 3: “intended function” Definition
The intended function for each ERCOT Transmission Operator restoration plan is to, as applicable
  Prepare transmission to allow Black Start Resource(s) to come online;
  Energize the Cranking Path(s), as available, to the next start Resource(s);
  Provide offsite power to additional generation and/or provide stabilizing load to control voltages and frequency within acceptable operating limits;
  Energize the Synchronization Corridor(s) to the synchronization points between Islands, as available;
  Coordinate with ERCOT on synchronizing Islands at the synchronization points; and
  Continue to follow ERCOT Reliability Coordinator directives as the restoration continues.