## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: March Meeting
Met Mar 28, 2013
23 members representing 15 companies as well as ERCOT & TRE.
System oscillations
NPRR 524
NPRR 527
SCR 773
EPG report review
Sympathetic trip discussion
Event reviews
System Frequency review

## Slide 3: System Oscillations
Members reported system oscillations in Houston area
Risk is generator damage
PMU data is desired
Request of ROS:
  Evaluate the need for PMU data & system study
  Recommend ERCOT lead and coordinate PSS tuning & system oscillation RCA’s
  PDCWG members are available to provide input in to the issues that are being experienced

## Slide 4: NPRR 524 Resource Limits in Providing Ancillary Service
The PDCWG has consistently affirmed that capacity from generators providing RRS must be frequency responsive
If carrying RRS, the resource will not be dispatched to its HRL or the HSL
ERCOT comments strike most of the proposed language, but defined term “Frequency Responsive”
  Separate NPRR should be submitted
If there is power augmentation that is frequency responsive, qualification testing is recommended to validate frequency responsiveness

## Slide 5: NPRR 524 - vote
Options for ROS consideration
  Reject NPRR 524
  Endorse the ERCOT comments to NPRR 524

## Slide 6: NPRR 527 Required Combined Cycle Telemetry for Operational Awareness and PDCWG Analysis
NPRR proposes to add individual HSLs of combined cycle generators (each CT & ST of a configuration)
PDCWG recommended telemetering only the non-frequency responsive capacity
ERCOT will work to incorporate feedback and provide comments
Recommend “Tabling NPRR 527 to allow ERCOT time to incorporate PDCWG feedback and submit comments” (vote)

## Slide 7: SCR 773 update
Target to be in production by end of April
All configurable factors will be tested prior to implementation in production
K-factor will use average regulation of last 3-5 minutes (estimate)
SCED Oscillations are risk

## Slide 8: EPG Report Highlights
CPS1 – ERCOT showing an upward trend
CPS2 – ERCOT only interconnection to meet the CPS2 performance threshold with a gradual upward trend
Epsilon – ERCOT showing a downward trend

## Slide 9: Sympathetic Trips
Result of Arizona outage
New process being brainstormed
Reliability risk when sympathetic trips result in a total loss greater than the largest single contingency
Defining a sympathetic trip
  Desire to understand the process
  What is normal
  What triggers plant review when a generator trips

## Slide 10: Event Review
4 measurable events in March
Reviewed 2 events
  3/7/13 @17:05 loss of 781MW
    Passed @ B & B+30
    No issues noted
  3/18/13 @17:21 loss of 495MW
    Passed @ B & B+30
    Wind forecast error had negative impact on event
    PRC was low during event

## Slide 11: ERCOT Frequency Control Report
Sydney Niemeyer NRG Energy
April 1, 2013

## Slide 12
Very consistent performance. 4 days above 170. No days below 156.

## Slide 13
1 day at 100%. 13 days at 98% or higher.

## Slide 15
12 Month rolling average CPS1 = 165.23

## Slide 17
Another month (second) with no days’ RMS1 above 20 mHz.

## Slide 22: Time Error and TEC
Monitored daily time error change to observe any changes in pattern.
  ERCOT has averaged about 10 TECs each month in 2012, always for slow Time Error. Average of about -1.000 second per day time accumulation.
March had 5 TECs. (all slow)
  This is an average of one TEC every 6.20 days or an average of -0.424 seconds per day lost.
  TECs occurred on Mar 7 and 8, 15 and 16, 18, 20 and 21, 27.

## Slide 23
March Daily Time Error Change

## Slide 24
ERCOT TEC History - 2013

## Slide 30: Focus for 2013
Formal & documented review/report of frequency responsiveness for Power Augmentation on Combined Cycle Resources (train not individual unit)
Review regulation/GTBD deployment effectiveness
Study the impact of HSL/basepoint/generation deviation on compliance and reliability
Responsive Reserve requirements, qualification vs. compliance. (10min vs 16 second)
Standardized/consistent metrics for PFR analysis (BAL001-TRE).
Standardized/reasonable expectations for extreme events (2750MW or larger lost) – driven by NERC.
No performance required for nonpayment (freq. resp AS)
ERS impact review with appropriate ERCOT group. Target Q1-2014
PMU data understanding of implications
Pilot of fast frequency response – characterize & create evaluation process.
Work on realistic measurement of combined cycles

## Slide 31
Questions?