ERCOT Operations Report

March 2013 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 3/4/2013 21:47 | 59.824 | 104 | Unit trip with approximately 595 MW net. |
| 3/6/2013 0:05 | 59.879 | 44 | Multiple unit trips with approximately 520 MW net. |
| 3/7/2013 17:05 | 59.786 | 16 | Unit trip with approximately 805 MW net. |
| 3/15/2013 18:39 | 59.861 | 18 | Unit trip with approximately 530 MW net. |
| 3/16/2013 21:03 | 59.880 | 144 | Gen deviation of approximately -1000 MW in 8 mins. |
| 3/17/2013 22:04 | 59.893 | 14 | Gen deviation of approximately -850 MW in 5 mins. |
| 3/18/2013 17:21 | 59.858 | 38 | Unit trip with 505 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

None

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 3/3/13 14:05:30 | 3/3/13 14:07:50 | 0:02:20 | 430.1 | Gen Deviation of approximately -800 MW in 5 mins. |
| 3/4/13 21:47:54 | 3/4/13 21:50:54 | 0:03:00 | 555.25 |  |
| 3/6/13 0:05:26 | 3/6/13 0:08:54 | 0:03:28 | 611.52 |  |
| 3/6/13 12:01:50 | 3/6/13 12:03:58 | 0:02:08 | 163.7 | Unit trip with 396 MW net. |
| 3/7/13 17:05:58 | 3/7/13 17:08:42 | 0:02:44 | 613.56 |  |
| 3/8/13 10:05:38 | 3/9/13 10:08:02 | 0:02:24 | 409.93 | Multiple unit trips with 520 MW net online. |
| 3/10/13 19:44:34 | 3/10/13 19:54:38 | 0:10:04 | 430.1 | Gen Deviation of approximately -1000 MW in 10 mins. |
| 3/15/13 18:39:56 | 3/15/13 18:42:00 | 0:02:04 | 174.87 |  |
| 3/16/13 21:02:28 | 3/16/13 21:07:45 | 0:05:17 | 598.08 |  |
| 3/17/13 22:04:30 | 3/17/13 22:07:17 | 0:02:47 | 510.72 |  |
| 3/18/13 17:21:28 | 3/18/13 17:23:53 | 0:02:25 | 322.93 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345 kV | Fort Worth Substation - Teasley Substation 138 kV | 19 | N |
| Asphalt Mines - Uvalde AEP & Odlaw Switchyard 138 kV | Hamilton Road - Maverick 138 kV | 18 | N |
| Aspermont AEP - Spur 138 kV | Wolfgang - Rotan 69 kV | 14 | N |
| Fort Stockton Plant - Barrilla 138 kV | Fort Stockton Switch - Barrilla 69 kV | 11 | N |
| Vernon 138_69t1 138/69 kV | Lake Pauline 138_69_1 138/69 kV | 10 | N |
| Pawnee Switching Station - Lon Hill 345 kV | Rinco - Airco AEP 138 kV | 9 | N |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 9 | N |
| Bosque Switch - Elm Mott 345 kV | Elm Mott - Rogers Hill BEPC 138 kV | 9 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Brown Switch - Killeen Switch 345 kV (35090) | 7 | N |
| Odessa North Axfmr1 138/69 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 7 | N |
| Pawnee Switching Station - Lon Hill 345 kV | Laquinta - Lobo 138 kV | 6 | N |
| Nelson Sharpe - Lon Hill 345 kV | Kingsville - Kleberg AEP 138 kV | 6 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Brown Switch - Killeen Switch 345 kV (35095) | 5 | N |
| Comanche Switch (Oncor) - Brown Switch 345 kV | Brown Switch - Killeen Switch 345 kV (35090) | 5 | N |
| Ennis Creek Switch - Knapp 138 kV | Sacroc - Snyder 138kV | 5 | N |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Kleberg AEP 138 kV | 4 | N |
| Falcon Seaboard - Morgan Creek SES 345 kV | Spraberry Switch - Midland Downtown 138 kV | 4 | N |
| Bosque Switch - Whitney 138 kV | Lake Whitney TNP - Whitney 138 kV | 4 | N |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 4 | N |
| Aspermont AEP - Spur 138 kV | Spur 138_69_1 138/69kV | 3 | N |
| Basecase | Laquinta - Lobo 138 kV | 3 | N |
| Comanche Switch (Oncor) - Brown Switch 345 kV | Brown Switch - Killeen Switch 345 kV (35095) | 3 | N |
| Coleto Creek - Pawnee Switching Station 345 kV | Coleto Creek - Kenedy Swtich 138 kV | 3 | N |
| Pawnee Switching Station - Lon Hill 345 kV | Rinco - Bonnieview 69 kV | 2 |  |
| Basecase | South Trent Wind Farm - Eskota Switch 138 kV | 2 |  |
| Basecase | Anacacho - Odlaw Switchyard 138 kV | 2 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | Stanton East - Martin Capacitor 69 kV | 2 |  |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney TNP 138 kV | 2 |  |
| DCKT Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Brown Switch - Killeen Switch 345 kV (35090) | 2 |  |
| DCKT Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Brown Switch - Killeen Switch 345 kV (35095) | 2 |  |
| DCKT W.A. Parish - Obrien 345 kV | Polk - Downtown 138 kV | 2 |  |
| DCKT W.A. Parish - Obrien 345 kV | Garrott - Midtown 138 kV | 2 |  |
| Midland East - Moss Switch 345 kV | Midland West - Windwood 138 kV | 2 |  |
| Midland East - Moss Switch 345 kV | Odessa EHV Switch- Big Three Odessa Tap 138 kV | 2 |  |
| South Lane City - Dyann 138 kV | Wallis - Sealy 138 kV | 2 |  |
| Laquinta - Lobo 138 kV | Falfur 138_69A1 138/69 kV | 2 |  |
| Eskota Switch Axfmr1 138/69 kV | Abilene Northwest - Ely Rea Tap 69 kV | 2 |  |
| Amoco South Foster - Westover 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 2 |  |
| Holt Switch - Moss Switch 138 kV | Odessa North - Odessa Basin Switch 69 kV | 2 |  |
| Synder - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 2 |  |
| Spur - Scurry Switch 138 kV | Wolfgang - Rotan 69 kV | 2 |  |
| Pawnee Switching Station - Lon Hill 345 kV | Sinton - Skidmore 69 kV | 1 |  |
| Aspermont AEP - Spur 138 kV | Roby - Rotan 69 kV | 1 |  |
| Nelson Sharpe - Lon Hill 345kV | Nelson Sharpe 138_PS 138 kV | 1 |  |
| Vernon 138_69t1 138/69 kV | Lake Pauline - Liberty Rea 69 kV | 1 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | Spraberry Switch AXFMR1 138/69 kV | 1 |  |
| Coleto Creek - Pawnee Switching Station 345 kV | Fallscty - Kenedy Switch 138 kV | 1 |  |
| Coleto Creek - Pawnee Switching Station 345 kV | Victoria - Loop 463 Sub 138 kV | 1 |  |
| South Lane City - Dyann 138 kV | Sealy - Peters 138 kV | 1 |  |
| Laquinta - Lobo 138 kV | Laquinta - Bruni Tap 138kV | 1 |  |
| DCKT Brown Switch - Killeen Switch 345 kV | San Angelo Power Sation - Yellow Jacket 138 kV | 1 |  |
| DCKT Brown Switch - Killeen Switch 345 kV | Sonora - Friess Ranch 69 kV | 1 |  |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Highlands TNP - West TNP 138 kV | 1 |  |
| DCKT Marion - Zorn and Clear Springs 345 kV | Marion 24AT2 345/138 kV | 1 |  |
| DCKT South Channel-Pair & Shell 138kV | Conial - Waburn 138 kV | 1 |  |
| Lobo - San Miguel 345_138 KV Switchyards 345 kV | Asherton - Catarina 138 kV (Ashert_Catari1) | 1 |  |
| San Miguel 345_138 KV Switchyards Auto_H 345/138kV | Laquinta - Lobo 138 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | San Diego - Freer 69 kV | 1 |  |
| Pawnee Switching Station - San Miguel 345_138 kV Switchyard 345 kV | Laquinta - Lobo 138 kV | 1 |  |
| Snyder - China Grove Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| DCKT Cedar Bayou Plant - Chambers & North Belt 345 kV | Jefferson - South Channel 138 kV | 1 |  |
| Texas Gulf Sulphur - South Lane City 138 kV | Altair - Stafford 69 kV | 1 |  |
| Pelican - Lon Hill 138 kV | Rinco - Airco AEP 138 kV | 1 |  |
| Gaf TNP - Greenbelt TNP 138 kV | Greenbelt TNP - Tejas TNP 138 kV | 1 |  |
| San Angelo Paulann - San Angelo Red Creek 138kV | San Angelo Red Creek - Ben Ficklin 138kV | 1 |  |
| Orange Grove Switching Station - Lon Hill 138 kV | Smith - Edroy 69kV | 1 |  |
| Los Fresnos - Loma Alta Sub 138 kV | Port Isabel - South Carbide 138 kV | 1 |  |
| North Weslaco - North Mercedes 138 kV | Weskica Switch - Weslaco Sub 138 kV | 1 |  |
| Koch Up Rriver - Gila 138 kV | Gila - Hiway 9 138kV | 1 |  |
| Morgan Creek SES Axfmr2l (3) 345/138 kV | Morgan Creek SES Axfmr4l (3) 345/138 kV | 1 |  |
| DCKT Chambers - King and Cedar Bayou Plant - North Belt 345 kV | Exxon - Lynch 138kV | 1 |  |
| DCKT Comanche Peak SES Units 1 & 2 | Laquinta - Lobo 138 kV | 1 |  |
| Kleberg AEP - Loyola 138 kV | Loyola Sub 138_69_1 138/69 kV | 1 |  |
| DCKT Cagnon - Calavers & Braunig 345 kV | Skyline - Calavers 345 kV | 1 |  |
| Vernon - Oklaunion 138 kV | Lake Pauline 138_69_1 138/69 kV | 1 |  |
| DCKT Royse Switch - Forney Switch 345 kV | Forney Switch AXFMR3H 345/138 kV | 1 |  |
| Paint Creek - Graham SES 138 kV | Orlando - Vernon 138 kV | 1 |  |
| Bracketville to Odlaw Switch 138 kV | Hamilton Road - Maverick 138 kV | 1 |  |
| Gila - Hiway 9 138 kV | Gila - Hiway 9 138 kV | 1 |  |
| Hiway 9 - Citigo N Oak Park 138 kV | Nueces Bay - Morris Street 138 kV | 1 |  |
| Morgan Creek SES Axfmr4l (3) 345/138 kV | Morgan Creek SES Axfmr2l (3) 345/138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which met our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 9 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

- None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 03/01/2013 | Transmission and Security Desk V1 Rev 22 | 623 |
| 03/01/2013 | Shift Supervisor Desk V1 Rev 19 | 622 |
| 03/01/2013 | Resource Desk V1 rev 21 | 621 |
| 03/01/2013 | Reliability Unit Commitment V1 Rev 18 | 620 |
| 03/01/2013 | Real Time Desk V1 Rev 22 | 619 |
| 03/01/2013 | DC Tie Desk V1 Rev 18 | 618 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

03/26 08:00 41,687 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 | 2.83 |
| March | 2.24 | 2.02 | 3.49 | 2.68 |
| April | 2.47 | 3.55 | 2.78 |  |
| May | 2.63 | 3.27 | 3.09 |  |
| June | 2.84 | 2.28 | 2.85 |  |
| July | 2.39 | 1.63 | 2.85 |  |
| August | 2.29 | 2.28 | 2.96 |  |
| September | 3.14 | 2.70 | 3.43 |  |
| October | 2.37 | 3.51 | 2.99 |  |
| November | 3.46 | 3.38 | 2.90 |  |
| December | 2.60 | 2.99 | 3.47 |  |
| Annual Average | 2.83 | 2.83 | 3.02 | 3.00 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 3/11/2013 | 07:28 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/16/2013 | 21:08 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

None

Watch

None

Emergency Notice

None

Texas RE Event Analysis

03/10 10:00 	ERCOT experienced the simultaneous loss of four 138 kV and four 69 kV lines due to weather in West Columbia area. This resulted in losing approximately 198 MW of generation.