## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: Summary
Alternate solution to NPRR 429
Regulation bias update (NPRR 486)
SCR 773
Event reviews

## Slide 3: February Meeting
Met Feb 28, 2013
17 members representing 13 companies as well as ERCOT & TRE.
Frequency responsiveness for Power Augmentation on Combined Cycle Resources related to NPRR 429
HSL/base point/generation deviation related to NPRR 486
Event review
Next meeting Mar 28, 2013

## Slide 4: Frequency Responsiveness for Power Augmentation on Combined Cycle Resources
In response to a WMS request, the PDCWG reviewed NPRR 429 and could neither oppose or endorse the NPRR at this time
  The PDCWG will remove this NPRR from its agenda but will reconsider at the request of ROS.
The PDCWG supports the goal to allow Resources to operate in a range that allows for the proper deployment of the ancillary service capacity that is being reserved
  ERCOT is drafting NPRR language that may resolve some of the issues that NPRR 429 seeks to correct
  ERCOT to submit for the March PRS meeting
The PDCWG is currently working to resolve some of the issues that define the performance requirements of RRS

## Slide 5: HSL/basepoint/generation deviation
Generation deviation has been identified as one of the reasons for the regulation bias offset related to (NPRR 486)
  Driven by HSL errors, not following energy deployments (basepoints, regulation)
ERCOT LFC system is periodically being tuned
PDCWG action to review performance of each members generators and look for issues.

## Slide 6: Event Review
01-15-2013 10:04 – Loss of 740MW
  Passed B-point, Failed B+30 point
  Regulation fully deployed at time of event
  Few generators squelched
  Few generators were non performers
  Few generators were slow to respond
  Sympathetic trip was identified as main driver for the B+30 failure

## Slide 7: Event Review
01-31-2013 04:52
High frequency event
  DC tie ramp occurred during event
  Fully deployed down regulation
  Wind did respond to high frequency
  Some basepoints were noted to increase while frequency was high.
    ERCOT to evaluate this issue

## Slide 8: Focus for 2013
Formal & documented review/report of frequency responsiveness for Power Augmentation on Combined Cycle Resources (train not individual unit)
Review regulation/GTBD deployment effectiveness
Study the impact of HSL/basepoint/generation deviation on compliance and reliability
Responsive Reserve requirements, qualification vs. compliance. (10min vs 16 second)
Standardized/consistent metrics for PFR analysis (BAL001-TRE).
Standardized/reasonable expectations for extreme events (2750MW or larger lost) – driven by NERC.
No performance required for nonpayment (freq. resp AS)
ERS impact review with appropriate ERCOT group. Target Q1-2014
PMU data understanding of implications
Pilot of fast frequency response – characterize & create evaluation process.
Work on realistic measurement of combined cycles

## Slide 9
Questions?