## Slide 1: Generation Storage™: Tapping Texas’ Hidden, Flexible, Peak Capacity
Kelsey Southerland
Director of Government Relations
ksoutherland@tas.com

## Slide 2: Presentation Agenda
What is Generation Storage
  Market driver
  Evolution of TIC
  How it works
  An ERCOT case study
  Historical uses
  Today’s innovative redesigns according to market changes
  Unique value for ERCOT
Energy Storage & Generation Storage
  Energy Storage: The black box
  FERC determinations
    Comparison to CAES, comparison to Pumped Hydro
Conclusion

## Slide 3: Typical Generation Storage™ Project
TES Tank
Chiller Package
Coil Retrofit
Secondary
Pump Skid

## Slide 4: Generation Storage
Gas turbines only operate at 100% of their rated capacity when the temperature outside is 59F.
Inlet Air Temperature, degrees (F)
GT POWER OUTPUT
80%
85%
90%
95%
100%
105%
110%
40
45
50
55
60
65
70
75
80
85
% of Rated Capacity
RECOVERED POWER
By chilling the inlet air of the turbine to ISO, full capacity is restored.
ADDITIONAL POWER
By chilling below ISO and adding storage, even more MWs are generated, and storage ancillary services benefits are captured
TAS GENERATION STORAGE
ISO TURBINE RATING
95
100
90
As temperatures climb into the 90’s and beyond, greater than 10% of the capacity of the turbine disappears.
Notes: The following slide will show an animation of the system in action followed by this same chart to specifically show the flexible capacity opportunity. Generation Storage allows the generator to produce added capacity that is now flexible all along the diagnol slope of the temperature derate

## Slide 5: Generation Storage: It began with TIC
Turbine inlet chilling (TIC) is an advanced form of ‘inlet chilling’ in which electric chillers are used to chill the inlet air of a gas turbine
Strong market penetration worldwide: TAS alone has installed TIC on over 300 turbines
----------
Parasitic Load: To restore full capacity to a 500 MW facility, losing about 75 MW, the chilling power required is between 7 and 10 MW
Limited Flexibility: The system is mostly on or off, ranges are difficult to achieve
The evolution to Generation Storage begins…

## Slide 6: Generation Storage: How it works
Generation Storage is the TIC technology, version 2.0, in which the chilling system is integrated with storage
Electricity is used to run an electric chiller that chills water, typically during off-peak night hours
The chilled water is stored in a thermal energy storage tank
During on-peak hours, as the outside temperatures rise, the chilled water is released from the tank for the inlet air of the gas turbine to be passed across
The chilled water chills the inlet air to the gas turbine, generating additional megawatts than would have been possible without the chilled air;
*Thereby, the power originally used and stored in the form of chilled water, is regenerated and placed back upon the grid
  Power that would have been required to run the chillers during the on-peak hours of need is provided by off-peak power through storage
*In fact, due to the impact of the chilled water on the inlet air, the amount of power originally used and stored in the form of chilled water is re-generated, and additional power is generated as well

## Slide 7: GENERATION STORAGE™ (GS)
CHILLER PLANT
SECONDARY PUMP
PRIMARY PUMP
START
CHILLER
STOP
CHILLER
BURN CYCLE
BUILD CYCLE
TES TANK
UPPER DIFFUSER
LOWER DIFFUSER
GTG
START
PUMP
STOP
PUMP

## Slide 8: Typical Generation Storage™ Project
TES Tank
Chiller Package
Coil Retrofit
Secondary
Pump Skid
Customer: Electric Cooperative
Project Timing: 2008-2009
Outage Duration: ~15-30 Days
Construction Man-Hours: ~50,000
Construction Duration: ~9 Months
Turbine OEM: GE Frame 7FA
Power Plant Type: 2 x 1 Combined Cycle
Incremental Plant Output: ~65MW

## Slide 9: Historical Uses
Historically, TIC, and even Generation Storage, were seen solely as power augmentation systems; offering the ability for generators to maximize their capacity during the summer peak. As such, these systems were designed to operate ‘full throttle,’ providing the lowest temperatures for maximum output. The storage system reduced parasitic load, thereby offering more capacity when it was most needed
  Often times the systems were designed for partial storage with smaller chillers at full chilling capacity during peak hours
Furthermore, generators with Generation Storage systems historically have used station load to charge their tanks

## Slide 10: A New Grid, A New Market, Evolving Technology
Today, with:
  The integration of renewables and significant wind supply in TX
  Increasing peak demand without corresponding increase in peak supply, and
  The advancement of market systems
Markets value peak shifting, flexible capacity, and ancillary services
More than simply power augmentation, Generation Storage could and should provide traditional storage benefits to the grid as well including ancillary services: flexible capacity; regulation up/down
Customers have begun inquiring whether Generation Storage is treated like other storage systems and offered wholesale load treatment:
  These potential customers are interested in offering renewable integration services (utilizing night wind and prices for peak hour contribution)
  Providing more significant ancillary services capabilities
If offered the same treatment as other storage providers, these systems will be designed to provide more services, utilizing full storage rather than partial

## Slide 11: More Than Just Capacity
CHILLER PLANT
SECONDARY PUMP
PRIMARY PUMP
START
CHILLER
STOP
CHILLER
BURN CYCLE
BUILD CYCLE
TES TANK
UPPER DIFFUSER
LOWER DIFFUSER
GTG
START
PUMP
STOP
PUMP
Simply adjust the pump for the full range of power according to grid need- under two min response, no heavy maintenance impact

## Slide 12: Generation Storage™
Utilizing the storage tank, a generator could provide quick, grid
dispatchable, regulation up/down capability (under ten minutes) through simple
pump adjustment of water flowing out of the tank (ideal for renewable integration).
80%
85%
90%
95%
100%
105%
110%
40
45
50
55
60
65
70
75
80
85
90
95
100
Inlet Air Temperature, degrees (F)
% of Rated Capacity
RECOVERED POWER
GT POWER OUTPUT
ADDITIONAL POWER
ISO TURBINE RATING

## Slide 13: Today’s Value in Using Grid Power
For generators,
  the ability to use wholesale power to charge the TES tank provides next day storage services through added flexible capacity and ancillary services even if the generator itself is powered down overnight, or for several nights
  At times, the cost to generate electricity may be greater than the cost of wholesale power
For the grid,
  When wind power overwhelms the grid and there is need for a load sink, a generator could activate the chillers and storage tank to capture that power for peak time use in the future

## Slide 14: Unique Value in ERCOT
Generation Storage provides the most value, in ERCOT:
  High temperatures/long ‘summer’
    High summer peak
  Power supply > 50% gas generation
  Incredible wind penetration at night
  Humid climate in much of the state
Over 2,500 MWs are lost to hot temperatures in Texas every summer
  Generation Storage can recover those lost megawatts utilizing valuable Texas wind generated at night
  Generators can find a new value stream and offer more complex services to the grid with their existing assets through incorporating storage

## Slide 15: ENERGY STORAGE & GENERATOR CHILLED STORAGE

## Slide 16: Energy Storage: The Black Box
ELECTRIC ENERGY IN
ELECTRIC ENERGY OUT
ELECTRIC ENERGY NOT USED FOR CONSUMPTION
Batteries
Pumped Hydro
Flywheels
CAES
It is this conversion/storage cycle that distinguishes energy storage facilities…from facilities that consume electricity

## Slide 17: GCS Comparison with CAES
CAES:
Electric Energy Compressor Compressed Air is Stored Compressed Air and Gas enter Turbine Electric Energy is Generated
GCS:
Electric Energy Chiller Chilled Water is Stored Chilled Water exchanges with Inlet Air, Chilled Inlet Air and Fuel enter Turbine Electric Energy is Generated

## Slide 18: Highlights from FERC 2001 Ruling*
“…As the Applicant notes, the use of compressed air as a medium for the storage of energy in an energy storage facility is a new technology. However, we find that a compressed air energy storage facility is analogous to a pumped storage hydroelectric facility, in that compressed air is used in a conversion/storage cycle just as water is used in a pumped storage hydroelectric facility in the conversion/storage cycle. We also find that, given the similarities between the facilities, it is appropriate to afford compressed air energy storage facilities the same regulatory treatment this Commission traditionally has afforded pumped storage hydroelectric facilities, namely, that deliveries of pumping energy as part of an off-peak/on-peak energy exchange transaction are considered to be exclusively wholesale transactions.”
“…the Commission views the pumping energy not as being consumed, but rather as being converted and stored, as water in the upper reservoir, for later re-conversion (during on-peak hours when demand is high) back to electric energy. It is this conversion/storage cycle that distinguishes energy storage facilities, whether pumped storage hydroelectric facilities or compressed air energy storage facilities, from facilities that consume electricity (in the form of station power or otherwise).”
Issued June 29, 2011 for Norton Energy Storage Docket No. EL01-70-000

## Slide 19: Conclusion
ELECTRIC ENERGY IN
ELECTRIC ENERGY OUT
ELECTRIC ENERGY NOT USED FOR CONSUMPTION
Batteries
Pumped Hydro
Flywheels
CAES
…Generator Chilled Storage
1 MwHr OFF-PEAK
electricity
in
~8 MwHrs
ON-PEAK
electricity
out
*8 to 1 output due to increased mass flow rate of turbine, and addition of more gas- storage provides off peak to on peak shift and full range of flexible capacity/ancillary services