## Slide 1: Discussion of AEP Analysis of West Texas Congestion and Rule Change
Kris Dixit

## Slide 2: Agenda
The Task was to provide an analysis to support or disprove AEP’s Premise concerning Same Transmission Elements.
AEP Proposal and Premise
Analytical basis of AEP Premise
Questioning AEP Premise
Real Time Network Topology Shift Factors
Conclusions from Real Time Shift Factors
ERCOT actions to mitigate Congestion
Summary of Issues

## Slide 3: AEP Proposal and Premise
Proposal:
When one contingency constraint pair is deemed irresolvable, designate the same constraint irresolvable for all other contingencies (for the same direction of flow)
Total net margin tracked for one constraint is tracked for the entire family of contingencies for that constraint
Place a shadow price cap in DAM to limit DAM prices from getting higher in the event of an expected irresolvable constraint in the RT
Premise:
Constraints that are occurring for different contingencies (in the same direction) tend to have generators with either the same or similar shift factors to that constraint.
These shift factors tend to be correlated within a 90% band of values

## Slide 4: Analytical basis of AEP Premise
AEP/Utilicast approached the analysis by looking at one steady state case. The Feb 2012 CRR base-case to carry out the analysis.
This analysis was done by calculating shift factors of each generator to a distributed load bus for each of the constraint/contingency pairs within that base case.
This analytical process yielded results where generation shift factors on the same constraint in the same direction for different contingencies fell within a very tight band of values, and were highly correlated
This result supported the argument that constraints for different contingencies tend to behave similarly and should be treated similarly

## Slide 5: Questioning AEP’s Premise
Premise is conceptually flawed because generation shift factors on constraints tend to vary depending on changes to network model
To do the analysis for AEP’s proposal, a steady state case would have to be chosen, that adequately represents all potential network scenarios. It would be fundamentally difficult to do so. Any one case cannot represent the spectrum of shift factors that could occur on a constraint.
Convergence between the RT and DAM is critically important for proper functioning of the nodal market and setting Shadow price caps in the DAM is unnecessary. DAM is a financial market in which Buyers and Sellers participate causing the market to converge based upon the markets expectation of the RT prices. It works. If there is a cap established for the RT the market will converge to that cap in the DAM.

## Slide 6: Real Time Network Topology Shift Factors
ERCOT posts real time generator shift factors on a 5 minute basis for every contingency constraint pair in SCED
  This allows us to collect data (shift factors) for a broad range of network topology scenarios. As opposed to a single set of shift factors calculated from a single steady state case as in AEP analysis.
The data lists all the generators and their associated shift factors on a contingency/constraint pair currently binding in SCED
These shift factors are calculated based on the network model of the system at that time, and represent the most accurate shift factor calculations available.
Our goal was to test AEP/Utilicast’s hypothesis with these shift factors. If the hypothesis is correct, we should see a high degree of correlation on shift factors for constraints for a family of contingencies
We calculated the average shift factors (Jan 2012 to April 2013) for each contingency constraint pair and compared that with the average shift factors for other contingencies for the same constraint
To quantify the correlation we normalized the averages to the minimum shift factor. (shift factor for a given contingency as a percentage of the minimum shift factor of that generator on that constraint across all contingencies.)
We specifically looked at the top ten constraints that AEP highlighted in their analysis

## Slide 7: Data for 6215__A China Grove to Bluff Creek

## Slide 8: Conclusions from Real Time Shift Factors
Generation shift factors tend to vary quite a bit when changes occur to the network topology, even to the extent that they flip from positive to negative.
These differences tend to cause different prices at generation nodes
Grouping all contingency/constraint pairs into one irresolvable list with a collective net margin calculation, as proposed by AEP, amounts to picking “Winners and Losers” because the prices of a node will depend upon when a particular constraint is active as compared to other constraints in its “Family of Similar Constraints” or “Same Transmission Element”.
  A specific generator may have a positive shift factor to a constraint for one contingency and may have a negative shift factor for a different contingency.
  Depending on which contingency/constraint pair is binding, total net margin would add up, which may significantly favor one generator over the other
  A shadow price change after that would then impact other generators that now have a greater impact on the counter flow for that constraint for a different contingency
Any rule that tries to group contingencies with either one or multiple constraints should fail, because of the fluidity in network topology
  It fails to provide appropriate price signals
  The subsequent premature reduction in shadow price caps reduces SCED’s ability to manage congestion through the use of base points to generators with low shift factors on the constraint. This in turn will result in manual dispatch instructions causing uplift.

## Slide 9: ERCOT actions to mitigate congestion
ERCOT already takes specific actions that mitigate congestion and pricing when there are multiple constraint/contingency pairs involved
For the same contingency when there are multiple constraints binding, ERCOT only activates one of them, based on the premise that relieving one will relieve all.
  Doing so, eliminates the possibility of compounding the cost of the shadow prices
For different contingencies, if ERCOT deems that generation shift factors are substantially similar for the same constraint, ERCOT tends to deactivate all but one of the constraints, under the same premise as above
  Example: April 4th 2013, ERCOT deactivated all but one MGSES overload, despite the fact that they were binding for different contingencies.

## Slide 10: Summary of Issues with AEP proposal
Consistent high degree of correlation on generation shift factors for different contingency/constraint pairs has not been observed in the RT shift factors posted by ERCOT.
The proposal directly impacts the value of CRRs that have been currently sold through Dec 2014.
  Any changes to the Shadow price business practices should only be considered starting 2015, to respect the property rights of current CRR holders
There is no need to cap DAM shadow prices

## Slide 11: Alternative Approaches Explored
Contingency/constraint pairs could be grouped based on their shift factor on load buses
  Every load bus (like every generator bus) has a shift factor on every contingency constraint pair
  Shift factors should still vary depending on changes to network topology, unless the load zone is very small.
Reduce the value of the shadow price cap
  SCED would not resolve constraints
  It’s a move back to zonal and uplifting congestion cost.
Conclude that we should stay with the Holistic Solution
  Loads can effectively hedge congestions.
  Loads are reimbursed most of the cost of the hedge via CRR Auction Revenues
  Minimizing changes to congestion management will increase confidence in the fidelity of the ERCOT nodal market

## Slide 12: APPENDIX

## Slide 13: Data for MGSES_MR1H Morgan Creek Auto

## Slide 14: Data for ODNTH_FMR1 Odessa North Auto

## Slide 15: Data for 6474__A Morgan Switch to Sun Switch

## Slide 16: Data for 6430__C Moss to Anctp 138kV line

## Slide 17: April 4 2013 Congestion on Morgan Creek Auto

## Slide 18: Example of bi-directional flow Data for 6474__A Morgan Switch to Sun Switch