## Slide 1: Update on ERCOT Pilot Project for Fast Responding Regulation Service (FRRS)
TAC
May 2, 2013

## Slide 2: Objective
Overview
FRRS-up Response to sudden large low Frequency Events
Measuring ERCOT deployed FRRS-up against rate of change of Regulation-up deployment
Next Steps
Stakeholder Review Process
Questions

## Slide 3: FRRS Pilot Overview
FRRS pilot deployments began on Feb. 25, 2013 at hour ending 11.
When the pilot began, there were 32 MW FRRS UP and 30 MW FRRS DOWN qualified to participate.
Additional 1 MW FRRS UP and DOWN began participating on Mar. 16, 2013.
All the qualified resources completed the qualification tests.
ERCOT has made FRRS parameter changes twice and more parameter changes are expected during the course of pilot.

## Slide 4: Log of Parameter Changes
FAST RESPONDING REGULATION SERVICE PILOT PROJECT PARAMETER SETTINGS |  |  | 
Effective Date and Time | Operating Day 2-25-13 HE 11 | Operating Day 3-30-13 HE 1 | Operating Day 4-13-13 HE 1
Band 1 High Trigger Frequency (Hz) | 60.03 | 60.02 | 60.025
Band 2 High Trigger Frequency (Hz) | 60.05 | 60.05 | 60.05
Band 3 High Trigger Frequency (Hz) | 60.09 | 60.09 | 60.09
Band 1 Low Trigger Frequency (Hz) | 59.97 | 59.98 | 59.975
Band 2 Low Trigger Frequency (Hz) | 59.95 | 59.95 | 59.95
Band 3 Low Trigger Frequency (Hz) | 59.91 | 59.91 | 59.91
Capacity Deployment in Band 1 (%) | 50 | 50 | 50
Maximum Deployment Time per Band (sec) | 120 | 60 | 60
Recall Interval (sec) | 12 | 12 | 12
Single Event Reset High Trigger Frequency (Hz) | 60.01 | 60.01 | 60.01
Single Event Reset Low Trigger Frequency (Hz) | 59.99 | 59.99 | 59.99

## Slide 5: Overview of FRRS-UP Awards

## Slide 6: Overview of FRRS-DN Awards

## Slide 7: Dollar Amounts

## Slide 8: Number of FRRS Deployments
59.97
59.98
59.975

## Slide 9
Simulation: Effect of FRRS on sudden large Frequency decay
FRRS-Up Full Deployment with 1 second delay after 59.91 Hz

## Slide 10: 03-07-2013 Event with high resolution data

## Slide 11: 03-15-2013 Event with high resolution data

## Slide 12: 04-09-2013 event with high resolution data

## Slide 13: 03-29-2013 High Frequency Event

## Slide 14: 03-30-2013 High Frequency Event

## Slide 15: Effect of FRRS-Up on Frequency and Reg-Up
Frequency FRRS-Up Deployed FRRS Response Regulation Deployed

## Slide 16: Effect of FRRS-Up on Frequency and Reg-Up…..cntd
Frequency FRRS-Up Deployed FRRS Response Regulation Deployed

## Slide 17: FRRS Impact on Reg-Up Deployments

## Slide 18: Next Steps
Continue to evaluate and share FRRS Pilot data with various stake-holder groups
Post Preliminary (3 month) report on Pilot in early June.
Perform cost benefit analysis prior to July 2013 Board meeting
Obtain feedback on cost benefit analysis approach.

## Slide 19: Stakeholder Review Process
In March and April, ERCOT presented and discussed updates on the FRRS-pilot with ETWG and PDCWG. (Actual performance data was reviewed.)
WMS -- May 8
ROS -- May 9
BOD -- May 14 (General update, Heads-up on decision required at July BOD meeting) Current Pilot end date is August 23, 2013.
Additional discussions planned for stakeholder meetings in June 2013
July BOD meeting - - provide options.

## Slide 20: Questions?