## Slide 1: AEP’s Response to EDF’s Analysis
Notes: <number>

## Slide 2: Apples vs. Oranges
EDF’s analysis technique compares apples to oranges
  Shift factors do change as the transmission model changes
  Shift Factors for constraints are only published when the constraint is active
  EDF’s technique (averaging published shift factors) compares different time periods with different outage sets/installed upgrades
  Using EDF’s Analysis premise, constraints are often not even similar to themselves

## Slide 3: Distorting with Divisors
EDF also “normalizes” the data by dividing by the minimum shift factor
Where the minimum shift factor is small this has the effect of exaggerating differences
  1.56% vs. 3.39% becomes 234% vs 510%

## Slide 4
FEB
APR
JUN
AUG
OCT
DEC
6215__A SCED China Grove to Bluff Creek constraint activity in 2012

## Slide 5: 6215__A China Grove to Bluff Creek 4/30/2013 Hour Ending 12
Shift Factors |  |  |  |  |  |  |  |  |  |  |  | 
 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
 | DANDNOT8 | DMGSLNG5 | DODEQAL5 | SACRLME9 | SCSEGLD8 | SFLCMDL5 | SFLCMGS5 | SGLDSUN8 | SMDFHLT8 | SSACSUN8 | SSNYCGR8 | SSUNMGS8
From Station | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138 | CGRSW_138
To Station | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138 | BCKSW_138
BULLCRK_1_2 | N/A | -53% | -53% | N/A | -52% | -53% | -53% | -73% | -54% | -55% | -54% | -56%
CSC_CSECG1_2 | N/A | -22% | -22% | N/A | -22% | -22% | -22% | -84% | -22% | -35% | -30% | -30%
BRAZ_WND_ALL | N/A | -18% | -18% | N/A | -17% | -17% | -17% | 3% | -18% | -32% | -27% | -26%
RDCAN_RDCNY1 | N/A | -16% | -16% | N/A | -16% | -16% | -16% | 3% | -17% | -30% | -25% | -24%
MWEC_G1 | N/A | -9% | -9% | N/A | -9% | -9% | -9% | 2% | -10% | -17% | -15% | -15%
WEC_WECG1 | N/A | -4% | -4% | N/A | -4% | -4% | -4% | 2% | -5% | -9% | -7% | -8%
ENAS_ENA1 | N/A | -2% | -2% | N/A | -2% | -2% | -2% | 4% | -3% | 10% | -14% | -7%
CARBN_BSP_1 | N/A | -1% | -1% | N/A | 0% | 0% | 0% | -2% | -1% | 1% | 0% | -1%
SGM_SIGNALMT | N/A | -1% | -1% | N/A | 0% | -1% | -1% | -2% | -1% | 0% | 0% | -1%
LONEWOLF_ALL | N/A | 0% | 0% | N/A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
ELB_ELBCREEK | N/A | -4% | 0% | N/A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
PC_SOUTH_ALL | N/A | -4% | 0% | N/A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
MGSES_CT123 | N/A | 1% | 1% | N/A | 1% | 1% | 1% | 1% | 1% | 2% | 2% | 2%
MGSES_CT456 | N/A | 1% | 1% | N/A | 1% | 1% | 1% | 1% | 1% | 2% | 2% | 2%

## Slide 6: Shift Factors are Materially Similar
Original correlation factor calculated over all buses
  EDF shows only buses fairly close to element, exaggerates differences
When looked at on the same model, even these buses have basically the same shift factors
Not perfect
  Some difference in SGLDSUN8 shift factors
  Easy to implement
  Better than what we have

## Slide 7: Purpose of Holistic Solution
Stop load from getting hammered by irresolvable structural inadequacy of grid
  Feb 2011 Ice Storm
Leave prices high enough to incent generation siting
Leave prices high enough for reasonable dispatch
This proposal furthers those aims by recognizing that the same irresolvable structural inadequacy can have slightly different names
  Still leaves prices high enough for all generators to be “winners”