ERCOT Operations Report

April 2013 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 4/2/2013 21:25 | 59.838 | 10 | Multiple unit trips with 810 MW net. |
| 4/9/2013 18:21 | 59.879 | 22 | Unit trip with 761 MW net. |
| 4/23/2013 11:19 | 59.865 | 25 | Unit trip with 600 MW net. |
| 4/24/2013 8:59 | 59.841 | 39 | Unit trip with 418 MW net. |
| 4/25/2013 11:37 | 59.819 | 219 | Frequency issue occurred as a result of the R2 EMS migration. Approx. 650 MW of generation dropped due to old base points being sent to the market. The root cause has been identified and corrected to prevent this from happening in future. |
| 4/26/2013 23:34 | 59.874 | 180 | Gen deviation of approx. -1400 MW in 6 min. |
| 4/29/2013 0:34 | 59.863 | 57 | Multiple unit trips with 750 MW net. |
| 4/29/2013 13:59 | 59.845 | 253 | Unit trip with 520 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 4/12/2013 20:34 | Local Voltage Oscillation | Approx. 6 hours | The event was caused by the incorrect setting of Park Power Control system at one wind farm. During the event, several PMUs close to the wind farm detected 2Hz oscillation from voltage magnitude signals. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 4/2/13 21:15:36 | 4/2/13 21:27:48 | 0:12:12 | 354.44 |  |
| 4/9/13 18:21:42 | 4/9/13 18:23:40 | 0:01:58 | 680.83 |  |
| 4/14/13 21:01:34 | 4/14/13 21:03:34 | 0:02:00 | 307.17 | Unit trip with 199 MW net. |
| 4/17/13 0:05:00 | 4/17/13 0:09:40 | 0:04:40 | 429.5 | Gen deviation of approx. -1400 MW in 8 mins |
| 4/23/13 11:19:32 | 4/23/13 11:22:04 | 0:02:32 | 286.5 |  |
| 4/24/13 8:59:38 | 4/24/13 9:02:10 | 0:02:32 | 469.84 |  |
| 4/25/13 11:41:35 | 4/25/13 11:42:28 | 0:00:53 | 670.11 |  |
| 4/26/13 13:45:36 | 4/26/13 13:53:00 | 0:07:24 | 453.33 | Unit trip with 268 MW net. |
| 4/26/13 21:02:20 | 4/26/13 21:04:16 | 0:01:56 | 249.71 | Gen deviation of approx. -700 MW in 3 mins |
| 4/26/13 23:34:16 | 4/26/13 23:41:20 | 0:07:04 | 642.23 |  |
| 4/29/13 0:03:56 | 4/29/13 0:08:00 | 0:04:04 | 456.97 | Unit trip with 520 MW net. |
| 4/29/13 0:34:40 | 4/29/13 0:38:12 | 0:03:32 | 389.85 |  |
| 4/29/13 13:59:20 | 4/29/13 14:08:16 | 0:08:56 | 694.45 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| Vernon 138_69t1 138/69 kV | Lake Pauline 138_69_1 138/69 kV | 17 | N |
| Asphalt Mines - Uvalde AEP & Odlaw Switchyard 138 kV | Hamilton Road - Maverick 138 kV | 17 | N |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 9 | N |
| Aspermont AEP - Spur 138 kV | Wolfgang - Rotan 69 kV | 8 | N |
| Aspermont AEP - Spur 138 kV | Spur 138_69_1 138/69 kV | 7 | N |
| Aspermont AEP - Spur 138 kV | Spur - Girard Tap 69 kV | 7 | N |
| Manual Morgan Creek SES Axfmr2h (3) 345/138 kV | Morgan Creek SES Axfmr1h (3) 345/138 kV | 7 | N |
| Fort Stockton Plant - Barrilla 138 kV | Fort Stockton Switch - Barrilla 69 kV | 7 | N |
| Rd Wells Interchange - West Denton 138 kV | Teasley Substation - Pockrus Substation 138 kV | 6 | N |
| Basecase | Nueces Bay - Gila 138 kV (Gila_Nbec8) | 5 | N |
| Nelson Sharpe - Lon Hill 345 kV | Kingsville - Kleberg AEP 138 kV | 5 | N |
| Rd Wells Interchange - West Denton 138 kV | Jim Christal Substation - North Denton Interchange 138 kV | 5 | N |
| West Denton - Roanoke Switch 345 kV | Jim Christal Substation - North Denton Interchange 138 kV | 5 | N |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Kleberg AEP 138 kV | 4 | N |
| DCKT Singleton - Zenith 345 kV | Singleton - Tomball 345 kV | 4 | N |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | Asherton - Catarina 138 kV (Ashert_Catari1) | 4 | N |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345 kV | Jim Christal Substation - North Denton Interchange 138 kV | 4 | N |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 3 | N |
| Laquinta - Lobo 138 kV | Laquinta - Bruni Tap 138 kV | 3 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Orlando - Vernon 138 kV | 3 | N |
| Meadow - Ph Robinson 345 kV | Alvin TNP - Freeway Park TNP 138 kV | 3 | N |
| Synder - Sun Switch 138 kV | Sun Switch - Morgan Creek SES 138 kV | 3 | N |
| Amoco South Foster - Westover 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 3 | N |
| DCKT Sweetwater East Switch - Bitter Creek & Champion Creek Switch 345 kV | Morgan Creek SES - Tonkawa Switch 345 kV | 3 | N |
| Gail Sub - Lamesa & Willow Valley Switch 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 3 | N |
| DCKT Garfield AEN - Hicross AEN & Onion Creek & Pilot Knob 138 kV | Garfield AEN - Stoney Ridge 138 kV | 3 | N |
| Basecase | Nueces Bay - Gila 138 kV (Gila_Nbec9) | 2 |  |
| Nelson Sharpe - Lon Hill 345 kV | Nelson Sharpe 138_PS 138 kV | 2 |  |
| Golden Switch - Sun Switch 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 2 |  |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | Laquinta - Lobo 138 kV | 2 |  |
| Aspermont AEP - Paint Creek 138 kV | Hamlin Shell - Aspermont Continental 69 kV | 2 |  |
| Aspermont AEP - Paint Creek 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 2 |  |
| Lobo 2_345_138_H 345/138 kV | San Diego - Freer 69 kV | 2 |  |
| DCKT Calaveras - Skyline & Walzem 138 kV | Five_Pts - Westside 138 kV | 2 |  |
| Victoria - Coleto Creek 138 kV (Coleto_Victor1) | Victoria - Coleto Creek 138 kV (Coleto_Victor2) | 2 |  |
| Bracketville to Odlaw Switch 138 kV | Hamilton Road - Maverick 138 kV | 2 |  |
| Oklaunion - Riley 345 kV (Okla_Riley2) | Lake Pauline 138_69_1 138/69 kV | 2 |  |
| McDonald Road - Big Spring Switch 138 kV | Forsan Tap - Crmwd 7 Tap 138 kV | 2 |  |
| Midland East - Moss Switch 345 kV | Odessa - Odessa North 138 kV | 2 |  |
| Coleto Creek - Pawnee Switching Station 345 kV | Coleto Creek - Kennedy Switch 138 kV | 2 |  |
| Morgan Creek SES Axfmr4l (3) 345/138 kV | Morgan Creek SES Axfmr1l (3) 345/138 kV | 2 |  |
| Rodd Field - Holly 138 kV | Airline AEP - Cabaniss 138 kV | 2 |  |
| Vernon 138_69t1 138/69 kV | Lake Pauline - Liberty Rea 69 kV | 1 |  |
| Basecase | Karsten At1_H 138/69 kV | 1 |  |
| Basecase | Dowgen Dow94 138 kV | 1 |  |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Nelson Sharpe 138 kV | 1 |  |
| Scurry Switch - Sun Switch 138 kV | Aspermont AEP 138_69T1 138/69 kV | 1 |  |
| Manual Morgan Creek SES Axfmr2h (3) 345/138 kV | Morgan Creek SES Axfmr1l (3) 345/138 kV | 1 |  |
| DCKT Singleton - Zenith 345 kV | Hockley - Betka 138 kV | 1 |  |
| DCKT Singleton - Zenith 345 kV | Roans Prairie - Kuykendahl 345 kV | 1 |  |
| DCKT Singleton - Zenith 345 kV | Kuykendahl - King 345 kV | 1 |  |
| Golden Switch - Sun Switch 138 kV | Willow Valley Switch - Gail Sub 138 kV | 1 |  |
| Laquinta - Lobo 138 kV | Falfur 138_69A1 138/69 kV | 1 |  |
| DCKT Lon Hill - Coleto Creek & Medio Creek - Lon Hill & Warburton Road Switching Station 345 kV | Rincon - Bonnieview 69 kV | 1 |  |
| DCKT Lon Hill - Coleto Creek & Medio Creek - Lon Hill & Warburton Road Switching Station 345 kV | Rincon - Airco AEP 138 kV | 1 |  |
| DCKT Lon Hill - Coleto Creek & Medio Creek - Lon Hill & Warburton Road Switching Station 345 kV | Kennedy Switch - Kennedy Sub 69 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | Asherton - Catarina 138 kV (Ashert_Catari1) | 1 |  |
| Spur - Scurry Switch 138 kV | Wolfgang - Rotan 69 kV | 1 |  |
| Spur - Scurry Switch 138 kV | Aspermont AEP 138_69T1 138/69 kV | 1 |  |
| Dyann - South Lane City 138 kV | Brazos Valley - Flewellen 138 kV | 1 |  |
| Morgan Creek SES Axfmr1h (3) 345/138 kV | Morgan Creek SES Axfmr4h (3) 345/138 kV | 1 |  |
| Scotland - Wichita Falls South Switch & Windthorst Switch 138 kV | Olney Xfmr22 138/69 kV | 1 |  |
| DCKT Trinidad SES - Stryker Creek SES & Mt Enterprise 345 kV | Gresham Road Switch - Stryker Creek SES 138 kV | 1 |  |
| Exxon Sharon Ridge - Bluff Creek Switch & Willow Valley Switch 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |  |
| Ennis Creek Switch - Knapp 138 kV | Sacroc - Snyder 138 kV | 1 |  |
| Lobo - Laredo Vft North 138 kV (Lardvn_lobo2) | Asherton - Catarina 138 kV (Ashert_Catari1) | 1 |  |
| DCKT Salado Switch - Killeen Switch 345 kV | Belton - Belton Southwest 138 kV | 1 |  |
| Morgan Creek SES Axfmr2h (3) 345/138 kV | Morgan Creek SES Axfmr1l (3) 345/138 kV | 1 |  |
| Odessa North Axfmr1 138/69 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |  |
| Hallettsville - Flatonia 138 kV | Gonzales Gvec - Shiner Gvec 69 kV | 1 |  |
| Los Fresnos - Loma Alta Sub 138 kV | La Palma - Villa Cavazos 138 kV | 1 |  |
| Meadow - Oasis 345 kV | Garrott - Midtown 138 kV | 1 |  |
| Comanche Switch (Oncor) - Brown Switch 345 kV | Brown Switch - Killeen Switch 345 kV (35090) | 1 |  |
| California Creek - Paint Creek & Fort Phantom Plant 138 kV | Lake Pauline 138_69_1 138/69 kV | 1 |  |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV | 1 |  |
| Mcneil LCRA - Gilleland 138 kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 1 |  |
| Ajo - Rio Hondo 345 kV | North Edinburg Nedin_XC2 345 kV | 1 |  |
| Dezavala - Hill Country 138 kV | Buckeye - L_A_Hts 138 kV | 1 |  |
| DCKT Marion - Zorn and Clear Springs 345 kV | Seguin - Seguin West 138 kV | 1 |  |
| Wink TNP Winkat1 138/69 kV | Wink Sub - Wink TNP 69 kV | 1 |  |
| Wink Sub - Permian Basin SES 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |  |
| Lytton Springs - Slaughter Lane 138 kV | Lytton Springs - Pilot Knob 138 kV | 1 |  |
| Barton Switch - Oran Sub 138 kV | Graham Switch - Graham 69 kV | 1 |  |
| Btu_Texas_Am - Btu_Atkins 138 kV | Grnprcs - Cssc 138 kV | 1 |  |
| DCKT Fayette Plant 2 - Lytton Springs & Holman AEN 345 kV | Austrop - Garfield LCRA 345 kV | 1 |  |
| Kirby - Bellaire & H O Clarke & Garrott (GT_KB_90) 138 kV | Downtown - Polk 138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which met our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 7 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

- None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

04/16 17:00 45,585 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 | 2.83 |
| March | 2.24 | 2.02 | 3.49 | 2.68 |
| April | 2.47 | 3.55 | 2.78 | 2.81 |
| May | 2.63 | 3.27 | 3.09 |  |
| June | 2.84 | 2.28 | 2.85 |  |
| July | 2.39 | 1.63 | 2.85 |  |
| August | 2.29 | 2.28 | 2.96 |  |
| September | 3.14 | 2.70 | 3.43 |  |
| October | 2.37 | 3.51 | 2.99 |  |
| November | 3.46 | 3.38 | 2.90 |  |
| December | 2.60 | 2.99 | 3.47 |  |
| Annual Average | 2.83 | 2.83 | 3.02 | 2.96 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 4/05/2013 | 06:52 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 4/28/2013 | 17:17 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 4/29/2013 | 13:18 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

None

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None