Black Start Working Group

Report to ROS

MAY 9th, 2013 Meeting

Primary Topic:  New NERC standard affects Black Start in ERCOT.

NERC EOP-005-2 becomes affective in the ERCOT region in July of 2013.  BSWG is reviewing EOP-005, Requirement 6, and how it affects Transmission Operators and ERCOT.

EOP-005-2 R6 states:

R6. Each Transmission Operator shall verify through analysis of actual events, steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed every five years at a minimum. Such analysis, simulations or testing shall verify: [Time Horizon = Long-term Planning] R6.1. The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. R6.2. The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. R6.3. The capability of generating resources required to control voltages and frequency within acceptable operating limits.

Topic 1 Resolution:

BSWG adopted a definition of “intended function” as seen in NERC EOP-005-2, R6.  This definition was developed to include all the intended functions of the TOP’s in the ERCOT region as related to Black Start.

The intent of this definition to clarify what the “intended function” is for the authors of Black Start Plans in the ERCOT region as well as preparing NERC audit evidence.

The “intended function” definition will appear in the Black Start template developed by ERCOT for Black Start Plan development.  This will be an addition to the ERCOT Operating Guide.

This definition will also be added to Op Guide Section 4.6 – Black Start Services.

The definition adopted by the BSWG is:

The intended function for each ERCOT Transmission Operator restoration plan is to, as applicable

  - Prepare transmission to allow Black Start Resource(s) to come online;

  - Energize the Cranking Path(s), as available, to the next start Resource(s);

  - Provide offsite power to additional generation and/or provide stabilizing load to control voltages and frequency within acceptable operating limits;

  - Energize the Synchronization Corridor(s) to the synchronization points between Islands, as available;

  - Coordinate with ERCOT on synchronizing Islands at the synchronization points; and

  - Continue to follow ERCOT Reliability Coordinator directives as the restoration continues.

This definition was scheduled for a ROS vote on the April 11th meeting.  At the April 8th BSWG meeting, a member voiced concern regarding the definition.  This member provided a formal request to table the vote for further discussion.  Additional members supported tabling the vote.  ROS agreed to table the vote to allow BSWG additional time to develop the definition.

BSWG continues to investigate the use of the ERCOT Black Start Simulator to provide evidence for NERC EOP-005-2, R6.  Use of the ERCOT Black Start Simulator for gathering NERC evidence for individual TOP’s has challenges.

As of the last BSWG meeting, ERCOT states that the Black Start Simulator will be available for gathering evidence for EOP-005-2 R6 in 2014.  The TOP’s present at the meeting indicated that they would be responsible for compliance in 2013.

The responsibilities for EOP-005-2 were not resolved at the TOP CFR meeting.  A committee representing the TOP’s recently met with TRE.  TRE indicated that R1 should be met using a dynamic study and R2/R3 could be met using a steady-state study.  BSWG will discuss this finding at the next BSWG on May 14th.

Additional Topic 2:

ERCOT Outage Coordination for Synchronization Corridors:

ERCOT now has the ability to monitor outages of synchronization corridors through the ERCOT Outage Scheduler.

The process includes:

- Generation of a daily report.  This is a 180 day report that includes all Black Start Resources and elements.

- This report is reviewed by ERCOT and when primary and secondary synchronization corridors are both out, ERCOT will coordinate with utility.

By monitoring these outages, ERCOT and transmission outage coordinators can limit the impact of system outages that affect the ERCOT Black Start Restoration Plan.

Additional Topic 3:

Black Start Template Proposed Changes - CenterPoint Energy

CenterPoint Energy has proposed changes to the Black Start template to help address NERC requirements and correct language.  The changes are currently under review by BSWG and will be discussed at the next BSWG meeting.

Pending Topics:

- Coordination with Gas Companies to provide station service to gas pumping facilities in the event of a Blackout.  This is necessary to restore fuel to many power plants and other critical facilities.  Meeting pending the signing of non-disclosure agreements for participants.

Next BSWG Meeting:  May 14, 2013