## Sheet1
Plan Type |  | Characteristics
| Execution Type | Do Operators Constrain? | If Constraining, which Rating is Used? | Can involve Loadshed? | Pre-Contingency Actions? | Developed for Outages? | Is "2 % Rule" Considered? | Modeled in MMS Apps? | If Modeled in MMS, how? | Considered in CRR? | If Considered in CRR, how? | Considered in DA Operations Studies? | If Considered in DA Operations Studies, how? | … | … | …
Remedial Action Plan | Manual SCADA Control | Yes | 15-Minute | No | No | No | Yes | Yes | Contingency Disabled | Yes | Ratings set to 9999 | Yes | EMS Processing
Mitigation Plan | Manual SCADA Control | Maybe | 2-Hour | Yes | No | No | Yes | No |  | No |  | Yes | Manual
Pre-Contingency Action Plan | Manual SCADA Control | No | N/A | No | Yes | No | No | No |  | No |  | Yes | Manual
Temporary Outage Action Plan | Manual SCADA Control | Maybe | 2-Hour | Yes | No | Yes | Yes | No |  | No |  | Yes | Manual
Special Protection System | Automatic Relay Action | Maybe | As Designed | No | Maybe | No | Yes | Yes | Contingency Disabled | Yes | Ratings set to 9999 | Yes | EMS Processing
…
…
…
Note on H5: Chad Thompson: 2% Rule refers to the 2% shift factor cut off hueristic employed by system operators whereby constraints which show no generator shift factors greater than 2% will not be passed to SCED.