## Slide 1: EFFECTIVE LOAD CARRYING CAPABILITY FOR WIND-POWER

## Slide 2: IT IS NOT ALL ABOUT ONE HOUR
WE SPEND A LOT OF MONEY ANALYZING ALL 8,760 HOURS TO DEVELOP A % OF PEAK RESERVE TARGET USING LOLP STUDIES
WHEN WE USE THE % TARGET DERIVED BY LOLP COMBINED WITH FORECASTED PEAKS THEN ALL THOSE OTHER HOURS ARE INTRINSICALLY INCLUDED
ERCOT’s CAPACITY SHORTAGES PERIODS OCCUR THROUGHOUT THE YEAR

## Slide 3: THE CDR/LOLP ARE AVERAGE
CDR LOAD FORECAST IS AVERAGE/NORMAL
RESOURCE SEASONAL RATINGS ARE FOR “AVERAGE” TEMPERATURES CONDITIONS
FINAL LOLP CURVE IS AN AVERAGE OF MANY WEATHER YEARS
LOLP FORCED OUTAGE ASSUMPTIONS ARE AVERAGE
LOLP MAINTENANCE OUTAGES ARE AVERAGE

## Slide 4: COMBINED CYCLE RATING vs TEMP

## Slide 5: Probability Weightings for Weather Years
Weather Year Probabilities based on NOAA data:
    Extreme summer weather with a 5% probability
      Composed of 2011
    Warmer than average with a 15% probability
      Composed of 2010
    Average weather with a 50% probability
      Composed of 25% for 2006 and 25% for 2009
    Cooler than average with a 25% probability
      Composed of 3.5714% for the following years: 1998 – 2000, 2003, 2005, 2007, 2008
    Much cooler than average with a 5% probability
      Composed of 1.25% for the following years: 1997, 2001, 2002, 2004
The impact of the likelihood of 2011 weather is seen in the graph on the next slide.

## Slide 6: Study Results
Study results are dependent on selection of probabilities for the 15 weather years, as shown in the following graph:

## Slide 7: ELCC SEEKS TO FIND A RATING EQUIVALENT TO A REFERENCE RESOURCE
ERCOT’s LOLP PROCESS USES A GAS TURBINE’s ANNUAL CHARACTERISTICS TO COMPARE WITH WIND-POWER’S ANNUAL CHARACTERISTICS
THE RATING THAT IS DERIVED HAS THE SAME RELIABILITY VALUE AS THE GAS TURBINES, INCLUDING FORCED AND PLANNED OUTAGES
THE BULK OF THE RELIABILITY CALCULATION FOCUSSES ON THE PEAK SUMMER SEASON

## Slide 8: ELCC AND % RESERVE ARE LINKED
THE LOLP vs % RESERVE CHART CANNOT BE CALCULATED WITHOUT KNOWING ELCC
TOTAL CAPACITY = EXITING CONVENTIONAL
+ ADDED/SUBTRACTED CONVENTIONAL
+ ELCC X WIND-POWER RATED CAPACITY
% RESERVE = ((TOTAL CAPACITY/PEAK LOAD) – 1) X 100

## Slide 9: ELCC AND % RESERVE ARE LINKED
IF ELCC IS LARGER THEN % RESERVE FOR 0.1 LOLP IS LARGER
100% OF ADDITIONAL WIND-POWER COUNTED IS COVERED BY ADDITIONAL RESERVE MW