ERCOT Operations Report

May 2013 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 5/3/2013 4:58 | 60.111 | 219 | Gen deviation of approximately +1125 MW during freq event. |
| 5/7/2013 3:07 | 59.853 | 20 | Unit trip with approximately 499 MW net. |
| 5/11/2013 20:13 | 59.866 | 18 | Unit trip with approximately 393 MW net. |
| 5/17/2013 13:38 | 59.878 | 10 | Unit trip with approximately 523 MW net. |
| 5/22/2013 16:11 | 59.744 | 460 | Unit trip with approximately 838 MW net. |
| 5/29/2013 23:47 | 59.824 | 59 | Unit trip with approximately 787 MW net. |
| 5/30/2013 14:46 | 59.855 | 189 | Unit trip with approximately 786 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 5/22/2013 16:11:16 | Unit Trip | Approx. 30 sec | The event was caused by the loss of one unit. The unit was generating 834 MW net before the trip, the frequency dropped to 59.74 Hz. The oscillating frequency of 0.65 Hz with 4.98% damping ratio was observed. |
| 5/29/2013 23:47:28 | Unit Trip | Approx. 52 sec | The event was caused by the loss of one unit. The unit was generating approximately 787 MW net before the trip, the frequency dropped to 59.82 Hz. Two oscillating frequencies of 0.12 Hz with 3.3% damping ratio and 0.25 Hz with 2.6% damping ratio were observed. |
| 5/30/2013 14:46:11 | Unit Trip | Approx. 184 sec | The event was caused by the loss of one unit. The unit was generating approximately 786 MW net before the trip, the frequency dropped to 59.85 Hz. The oscillating frequency of 0.98 Hz with 7.2% damping ratio was observed. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 5/7/13 3:07:28 | 5/7/13 3:11:44 | 0:04:16 | 316.45 |  |
| 5/11/13 20:13:54 | 5/11/13 20:16:06 | 0:02:12 | 322.06 |  |
| 5/17/13 13:38:28 | 5/17/13 13:41:24 | 0:02:56 | 179.31 |  |
| 5/19/13 23:06:08 | 5/19/13 23:12:12 | 0:06:04 | 371.57 | Gen Deviation of approximately -1700 MW net over a 6 min period. |
| 5/22/13 16:11:32 | 5/22/13 16:23:00 | 0:11:28 | 1491.8 |  |
| 5/29/13 23:47:38 | 5/29/13 23:50:22 | 0:02:44 | 156.37 |  |
| 5/30/13 14:46:22 | 5/30/13 14:51:38 | 0:05:16 | 632.29 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages (*)

| Contingency Description | Overloaded Element | Total |  |
| --- | --- | --- | --- |
| Morgan Creek Ses Axfmr2h (3) 345/138 kV | Morgan Creek Ses Axfmr1h 345/138kV | 19 |  |
| Meadow - Ph Robinson 345kV | Alvin Tnp - Freeway Park Tnp 138kV | 16 |  |
| Asphalt Mines - Uvalde Aep & Odlaw Switchyard 138kV | Hamilton Road - Maverick 138kV | 16 |  |
| DCKT Fayette Plant 2 - Lytton Springs & Holman Aen 345 kV | Lost Pines Aen - Austrop 345kV | 16 |  |
| Fort Stockton Plant - Barrilla 138kV | Fort Stockton Switch - Barrilla 69 kV | 14 |  |
| DCKT Garfield Aen - Hicross Aen & Onion Creek & Pilot Knob 138kV | Austrop - Daffin 138kV | 11 |  |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69kV | 9 |  |
| DCKT Singleton - Zenith 345kV | Singleton - Tomball 345kV | 9 |  |
| Vermon 138_69t1 138/69kV | Paul 138_69_1 138/69kV | 9 |  |
| Wink Tnp Winkat1 138/69kV | Wink Sub - Wink Tnp 69kV | 9 |  |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Laquinta - Lobo 138 kV | 8 |  |
| Amoco South Foster - Westover 138kV | Moss Switch - Amoco North Cowden Tap 138 kV | 8 |  |
| Mcneil Lcra - Gilleland 138kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 7 |  |
| Exxon Sharon Ridge - Bluff Creek Switch & Willow Valley Switch 138kV | Moss Switch - Amoco North Cowden Tap 138 kV | 7 |  |
| Lobo 2_345_138_H 345/138 KV | San Diego - Freer 69 kV | 7 |  |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | San Diego - Freer 69 kV | 6 |  |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 6 |  |
| Oklaunion - Riley 345kV (Okla_Riley2) | Paul 138_69_1 138/69kV | 6 |  |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345kV | 5 |  |
| DCKT Skyline - Calaveras 345kV | Cagnon AXFMR4H 345/138kV | 5 |  |
| Midland East - Moss Switch 345kV | Odessa - Odessa North 138kV | 5 |  |
| Big Wells - Dilley Switch Aep 138kV | West Batesville - Asherton 138kV | 5 |  |
| DCKT Benbrook Swtich - Sycamore Creek & Rocky Creek - Everman Switch 345kV | Edgecliff - Rogers Fort Worth 138kV | 5 |  |
| DCKT Odessa Ehv Switch - Longshore Switch & Quail Switch 345 kV | Forsan Tap - Crmwd 7 Tap 138 kV | 4 |  |
| DCKT Odessa Ehv Switch - Longshore Switch & Quail Switch 345 kV | McDonald Road - Forsan Tap 138kV | 4 |  |
| Gail Sub - Lamesa & Willow Valley Switch 138kV | Moss Switch - Amoco North Cowden Tap 138 kV | 4 |  |
| Aspermont Aep - Spur 138KV | Wolfgang - Rotan 69kV | 4 |  |
| Sydner - Sacroc 138kV | Ennis Creek Switch Axfmr1 138/69 kV | 4 |  |
| Laquinta - Lobo 138 kV | Laquinta - Bruni Tap 138kV | 4 |  |
| San Miguel 69kV Switch Yard - San Miguel 345_138kV Switchyards 138kV | Lytle Csw - Devine 69kV | 4 |  |
| Bosque Switch - Elm Mott 345kV | Rogers Hill Bepc - Elm Mott 138kV | 4 |  |
| Morgan Creek Ses Axfmr2h (3) 345/138 kV | Sterling City - Sterling County 69kV | 3 |  |
| DCKT Odessa Ehv Switch - Longshore Switch & Quail Switch 345 kV | China Grove Switch - Bluff Creek Switch 138 kV | 3 |  |
| Golden Switch - Sun Switch 138 kV | Ennis Creek Switch Axfmr1 138/69 kV | 3 |  |
| Ajo - Rio Hondo 345 KV | North Edinburg Nedin_XC2 345kV | 3 |  |
| DCKT Calaveras - Hotwells & To Laredo1 138kV | Calaveras - Skyline (N4_P3_1)138kV | 3 |  |
| Valero East - Air Liquid Aep 69kV | Koch Up River 138_69A1 138/69 kV | 3 |  |
| Clear Springs - Marion 345kV | Seguin - Seguin West 138 kV | 3 |  |
| Morgan Creek Ses Axfmr2h (3) 345/138 kV | Abilene Onyx Rea - Onyx Switching Station 69kV | 2 |  |
| Scurry Switch - Sun Switch 138 kV | Spur 138_69_1 138/69kV | 2 |  |
| Vermon - Oklaunion 138kV | Vermon - Grayback Tap 69kV | 2 |  |
| DCKT Cagnon - Calavers & Braunig 345 kV | Five_Pts - Wstside 138kV | 2 |  |
| DCKT Sweetwater East Switch - Bitter Creek & Champion Creek Switch 345kV | Morgon creek - Tonkawa Switch 345 KV | 2 |  |
| Wharton - Caney and Dyann 138kV | West Columbia - Angleton 138kV | 2 |  |
| DCKT Jewett - Singleton 345kV | Twin Oak Switch - Btu_Jack_Creek 345 KV | 2 |  |
| Sun Switch - Morgan Creek Ses 138kV | China Grove Switch - Bluff Creek Switch 138 kV | 2 |  |
| DCKT West Shackelford Station - Samsw & Navarro 345kV | Brown Switch - Killeen Switch 345kV (35090) | 2 |  |
| DCKT Lytton Springs - Holman Aen & Fayette Plant 2 345kV | Lost Pines Aen - Austrop 345kV | 2 |  |
| DCKT South Texas Project - Hillje & Whitepoint 345kV | Blessing - Lolita 138kV | 2 |  |
| DCKT Kirby - Bellaire & H O Clarke & Garrott (GT_KB_90) 138kV | Downtown - Polk 138kV | 2 |  |
| Btu_Atkins - Btu_Dansby 138kV | Btu_Nall_Lane - Btu_Braiacrest 69kV | 2 |  |
| Rd Wells Interchange - West Denton 138kV | Teasley Substation - Pockrus Substation 138kV | 2 |  |
| DCKT Marion - Zorn and Clear Springs 345 KV | Seguin - Seguin West 138 kV | 2 |  |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Blessing - Lolita 138kV | 2 |  |
| Nelson Sharpe - Lon Hill 345kV | Nelson Sharpe - Celanese Bishop 138kV | 2 |  |
| Bracketville to Odlaw Switch 138kV | Hamilton Road - Maverick 138kV | 2 |  |
| DCKT Fayette Plant 2 - Lytton Springs & Holman Aen 345 kV | Fayett 26AT2 345/138kV | 1 |  |
| Scurry Switch - Sun Switch 138 kV | Aspemont Aep - Aspermont Continental 69kV | 1 |  |
| Gail Sub - Lamesa & Willow Valley Switch 138kV | Holt Switch - Emma Tap 69 kV | 1 |  |
| Gail Sub - Lamesa & Willow Valley Switch 138kV | No Trees Switch - Dollarhide 138kV | 1 |  |
| Basecase | Nueces Bay - Gila 138kV (Gila_Nbec8) | 1 |  |
| Basecase | Nueces Bay - Gila 138kV (Gila_Nbec9) | 1 |  |
| Basecase | Ena Snyder Wind - Wkn_Bkr 69kV | 1 |  |
| Basecase | Anacacho - Odlaw Switchyard 138kV | 1 |  |
| Aspermont Aep - Spur 138KV | Spur - Girard Tap 69 kV | 1 |  |
| Exxon Sharon Ridge - Bluff Creek Switch & Willow Valley Switch 138kV | Big Spring Switch - Big Spring Crmwd Tap 69kV | 1 |  |
| Lobo 2_345_138_H 345/138 KV | Asherton - Catarina 138kV (Ashert_Catari1) | 1 |  |
| Sydner - Sacroc 138kV | Sun Switch - Morgan Creek SES 138 kV | 1 |  |
| Sydner - Sacroc 138kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| Big Wells - Dilley Switch Aep 138kV | Turtle Creek Switching Station - Crystal City 69 kV | 1 |  |
| Ajo - Rio Hondo 345 KV | Las Pulgas - Rio Hondo 138kV | 1 |  |
| Sun Switch - Morgan Creek Ses 138kV | Morgan Creek SES - China Grove Switch 138 kV | 1 |  |
| Salt Creek Bepc - Spur And Scurry Switch 138kV | Spur 138_69_1 138/69kV | 1 |  |
| Salt Creek Bepc - Spur And Scurry Switch 138kV | Wolfgang - Rotan 69kV | 1 |  |
| Salt Creek Bepc - Spur And Scurry Switch 138kV | Aspemont Aep - Aspermont Continental 69kV | 1 |  |
| DCKT Carrollton - Lewiswille Switch 345kV | Lewisville Switch Axfmr22 345/138kV | 1 |  |
| Ennis Creek Switch - Knapp 138 kV | Sacroc - Snyder 138kV | 1 |  |
| Salem Lcra At3 345/138kV | Fayett 26AT2 345/138kV | 1 |  |
| DCKT Brown Switch - Killeen Switch 345kV | Hamilton Road - Bracketville 138kV | 1 |  |
| DCKT Brown Switch - Killeen Switch 345kV | Sonora - Friend Ranch 138kV | 1 |  |
| DCKT Dewalt - Wa Parish & Karsten - H O Clarke 138kV | Karsten At1_H 138/69kV | 1 |  |
| Decordova - Comanche Peak Ses 345kV | Wolf Hollow 345 Switch - Rocky Creek 345kV | 1 |  |
| DCKT Elmcreek - San Miguel 345_138 Kv Switchyards 345kV | Lytle Csw - Devine 69kV | 1 |  |
| Asherton 138_69a1 138/69kV | Turtle Creek Switching Station - Crystal City 69 kV | 1 |  |
| West Columbia Main Tnp - West Columbia 138kV | West Columbia Main Tnp - West Columbia Local Tnp 138kV | 1 |  |
| Morgan Creek Ses Axfmr2h (3) 345/138 kV | Morgan Creek Ses Axfmr1h 345/138kV | 1 |  |
| Sydner Axfmr1 138/69kV | Sydner - Scurry Santa Fe Tap 69kV | 1 |  |
| DCKT Twin Buttes - Brown Switch & San Angelo Red Creek 345kV | Twin Buttes T1H (3) 345/138 kV | 1 |  |
| DCKT Twin Oak Switch - TNP One Plant 345kV | Brown Switch - Killeen Switch 345kV (35090) | 1 |  |
| Cabaniss - Airline Aep 138kV | Naval Base - North Padre 138kV | 1 |  |
| Obrien - Wa Parish 345kV (OB_WAP98) | Obrien - Wa Parish 345kV (OB_WAP99) | 1 |  |
| South Texas Project STP_G1 & STP_G2 | Clear Springs - Marion 345 kV | 1 |  |
| Coleto Creek - Pawnee Switching Station 345kV | Coleto Creek - Kenedy Swtich 138kV | 1 |  |
| China Grove Switch - Morgan Creek Ses 138 kV (6220) | China Grove Switch - Morgan Creek Ses 138 KV (6225) | 1 |  |
| Mesa View Swithc to Fort Lancaster 138kV | West Yates - Air Products Tap Aep 69kV | 1 |  |
| Baytown Energy Ctr to Chambers 138kV (BTECHB-1) | BTE AT-2_L 345/138kV | 1 |  |
| Fort Stockton Plant - Barrilla 138kV | Fort Stockton Switch - Barrilla 69 kV | 1 |  |
| Blessing - South Texas Project 345kV | Columbus - Stafhi 69kV | 1 |  |
| DCKT Parker Switch - Comanche Peak Ses 345kV | Comanche Peak Ses - Decordova Ses 345kV | 1 |  |
| DCKT Austrop -Garfield & Zorn 345kV | Austrop - Daffin 138kV | 1 |  |
| Bull Creek Wind - Willow Valley Switch 138kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| DCKT Elmcreek - San Miguel 345_138 Kv Switchyards 345kV | Lytle Csw - Devine 69kV | 1 |  |
| Laquinta - Lobo 138 kV | Laquinta - Bruni Tap 138kV | 1 |  |
| Crane Arco - Pegasus 138kV | Spraberry Switch - Skywest 138kV | 1 |  |
| Tenaska (Oncor) - Paris Switch 138kV | Paris East - Lamar Tap 138kV | 1 |  |
| Yellow Jacket - Fort Mason 138 kV | Fort Mason - Mason Aep 69 KV | 1 |  |
| Wink Tnp - Wink Sub 138kV | Wink Sub Axfmr1 138/69kV | 1 |  |
| Rd wells interchange Rdw_A1 138/69kV | Teasley Substation - Pockrus Substation 138kV | 1 |  |
| DCKT Chambers - King and Cedar Bayou Plant - North Belt 345kV | Cedar Bayou Plant AT3_H 345/138 kV | 1 |  |
| Hunt_ln - Cagnon 138kV | Five_Pts - Wstside 138kV | 1 |  |
| Rodd Field - Holly 138kV | Airline Aep - Cabaniss 138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which met our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 3 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

Annual Review completed in May:

1 RAP Created

Bandera – Leakey 69 kV line

6 RAPs Removed From Service

Carrollton Northwest - Lewisville Sw. Brazos 345 kV Single Circuit

Lewisville - Carrollton Northwest 138 kV Line

Lewisville Brazos 345/138 kV Autotransformer

Lewisville Sw. Brazos - Coppell 138kV Single Circuit (Lewisville Sw. Brazos - Lewisville Brazos)

Liggett Sw. 345/138 kV Autotransformer #1

Martin Lake - Elkton Martin Lake - Tyler Grande 345 kV Double Circuit

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

05/31 17:00 56,182 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 | 2.83 |
| March | 2.24 | 2.02 | 3.49 | 2.68 |
| April | 2.47 | 3.55 | 2.78 | 2.81 |
| May | 2.63 | 3.27 | 3.09 | 3.12 |
| June | 2.84 | 2.28 | 2.85 |  |
| July | 2.39 | 1.63 | 2.85 |  |
| August | 2.29 | 2.28 | 2.96 |  |
| September | 3.14 | 2.70 | 3.43 |  |
| October | 2.37 | 3.51 | 2.99 |  |
| November | 3.46 | 3.38 | 2.90 |  |
| December | 2.60 | 2.99 | 3.47 |  |
| Annual Average | 2.83 | 2.83 | 3.02 | 2.99 |

OCN, Advisory, Watch & Emergency Notices

Capacity

OCN

None

Advisory

| Date | Event |
| --- | --- |
| 5/8/2013 17:24 | ERCOT issued Advisory due to Voltage Security Assessment Tool (VSAT) has not solved in the last 30 minutes. |
| 5/29/2013 18:43 | ERCOT issued Advisory due to Voltage Security Assessment Tool (VSAT) has not solved in the last 30 minutes. |

Transmission Watch

| Date | Event |
| --- | --- |
| 5/8/2013 14:46 | ERCOT issued Transmission watch for the far west area due to several post-contingency overloads on the 69kV system. ERCOT requested that the Morgan Creek 345kV planned bus outage be returned to service. |
| 5/9/2013 17:55 | ERCOT issued Transmission watch for the Laredo Area due to a post-contingency loss of San Miguel to Lobo 345kV overloads Freer to San Diego 69kV line. Laredo DC-Tie schedule was curtailed to resolve the congestion. |
| 5/10/2013 14:44 | ERCOT issued Transmission watch for the Laredo Area due to a post-contingency loss of San Miguel to Lobo 345kV overloads Freer to San Diego 69kV line. Laredo DC-Tie schedule was curtailed to resolve the congestion. |
| 5/15/2013 11:39 | ERCOT issued Transmission watch for the Laredo Area due to a post-contingency loss of San Miguel to Lobo 345kV overloads Freer to San Diego 69kV line. Laredo DC-Tie schedule was curtailed to resolve the congestion. |
| 5/16/2013 11:39 | ERCOT issued Transmission watch for the Laredo Area due to a post-contingency loss of San Miguel to Lobo 345kV overloads Freer to San Diego 69kV line. Laredo DC-Tie schedule was curtailed to resolve the congestion. |
| 5/16/2013 16:14 | ERCOT issued Transmission watch for the Laredo Area due to a post-contingency loss of San Miguel to Lobo 345kV overloads Freer to San Diego 69kV line. Laredo DC-Tie schedule was curtailed to resolve the congestion. |
| 5/17/2013 10:50 | ERCOT issued Transmission watch due to a post-contingency loss of Big Wells to Dilley 138kV overloads the Crystal City to Turtle Creek 69kV line. Eagle Pass DC-Tie schedule was curtailed to resolve the congestion. |
| 5/21/2013 14:42 | ERCOT issued Transmission watch for the Laredo Area due to a post-contingency loss of San Miguel to Lobo 345kV overloads Freer to San Diego 69kV line. Laredo DC-Tie schedule was curtailed to resolve the congestion. |
| 5/22/2013 8:37 | ERCOT issued Transmission watch due to a post-contingency loss of Big Wells to Dilley 138kV overloads Asherton to West Batesville 138kV line. Eagle Pass DC-Tie schedule was curtailed to resolve the congestion. |
| 5/23/2013 7:44 | ERCOT issued Transmission watch due to a post-contingency loss of Big Wells to Dilley 138kV overloads Asherton to West Batesville 138kV line. Eagle Pass DC-Tie schedule was curtailed to resolve the congestion. |
| 5/23/2013 12:09 | ERCOT issued Transmission watch for the Laredo Area due to a post-contingency loss of San Miguel to Lobo 345kV overloads Freer to San Diego 69kV line. Laredo DC-Tie schedule was curtailed to resolve the congestion. |
| 5/30/2013 14:11 | ERCOT issued Transmission watch due to a post-contingency loss of Ajo to Rio Hondo 345kV overloads Las Pulgas to Rio Hondo 138kV line. Railroad DC-Tie schedule was curtailed to resolve the congestion. |

Watch

None

Emergency Notice

| Date | Event |
| --- | --- |
| 5/8/2013 16:57 | ERCOT issued Emergency Notice due to SCED failure. This was the result of an extended delay in the EMS and MMS database transition during a planned site failover. |

Texas RE Event Analysis

None