| PGRR Number | 031 | PGRR Title | Implement 95% Facility Rating Limit in the Planning Criteria |
| --- | --- | --- | --- |
| Date Posted | June 12, 2013 |

| Requested Resolution | Normal. |
| --- | --- |
| Planning Guide Section Requiring Revision | 4.1.1.2, Reliability Performance Criteria |
| Protocol Section(s) Requiring Revision | None. |
| Revision Description | This Planning Guide Revision Request (PGRR) changes the planning criteria such that system improvements are planned when studies show Facilities will be loaded up to 95% of their applicable rating. |
| Reason for Revision | The Operations and Planning Synchronization Task Force (OPSTF) identified several factors that could lead to overloads in operations that were not observed in planning studies. |

| Business Case |
| --- |
| 1 | Builds a margin into planning to address the following issues: Construction delays for projects planned to resolve a constraint could lead to overloads in Real-Time until the planned project is complete. This could occur for multiple summer seasons depending on the length of the delay. The current practice to test the unavailability of any given unit in planning studies may miss overloads that occur in operations when multiple units in an area are out of service or derated. Historically, over summer peak, as much as 10% of capacity in ERCOT has been either derated or unavailable. OPSTF analysis shows that this could increase loadings on circuits by 4% or higher. During severe weather that results in higher than anticipated temperatures and higher associated Load conditions, Facility thermal ratings are generally lowered for studies run by transmission operators per their ambient temperature adjusted dynamic ratings. As an example, one large Transmission Service Provider (TSP) noted that if the temperature were just 4°F higher than the assumed static rating temperature (104°F) the dynamically rated lines on their system would be rated 3% below the static rating. Since planning reliability studies use static ratings, overloads may be observed in operations under these conditions. Planning analysis utilizes Load forecasts made several years before the operating conditions are realized. Sometimes Load grows faster than anticipated and overloads occur in operations because the Load level was not seen soon enough in the planning analysis to get the necessary improvements constructed. For example, the recently completed 2012 Five-Year Transmission Plan identified 20 reliability problems for summer 2013 for which the transmission solution for those problems will not be constructed before the problems will occur. Planning analysis assumes that all Facilities are in-service. However, even over summer peak there is equipment that is out of service for maintenance, construction, or for an extended Forced Outage. This leads to line loadings in operations that are higher than anticipated in planning studies. Actual generation dispatch is different from that modeled in planning cases. |

| Sponsor |
| --- |
| Name | John Moore on behalf of the Planning Working Group (PLWG) |
| E-mail Address | John.moore@stratusenergy.com |
| Company | Stratus Energy |
| Phone Number | (512) 461-8679 |
| Cell Number |  |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |
| --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

Proposed Guide Language Revision

#### 4.1.1.2	Reliability Performance Criteria

(1)	The following performance criteria (summarized in Table 1, ERCOT-specific Reliability Performance Criteria, below) shall be applicable to planning analyses in the ERCOT Region:

(a)	With all Facilities in their normal state, following a common tower outage, all Facilities shall be within less than or equal to 95% of their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(b)	With any single generating unit unavailable, followed by Manual System Adjustments, followed by a common tower outage or the contingency loss of a transmission circuit or transformer, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(c)	With any single 345/138 kV transformer unavailable, followed by Manual System Adjustments, followed by a common tower outage, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, or FACTS device, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

(d)	Assessments, including proposed solutions, associated with criteria in paragraph (c), above, and line 3 of Table 1 below, shall be completed by no later than May 1, 2015.

(e)	With all Facilities in their normal state, following the contingency loss of a transmission circuit or transformer, all Facilities shall be less than or equal to 95% of their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(f)	For the conditions described in paragraphs (a) and (c) above, Facilities may be between 95% and 100% of their applicable Ratings if the loading on those Facilities is not expected to significantly change within the six-year planning horizon.  Examples of such Facilities may include transmission circuits that are radial to Generation Resources where the maximum output of the Generation Resources is not expected to increase within the six-year planning horizon and transmission circuits that are radial to Load that is not expected to significantly increase within the six-year planning horizon.

(g)	Assessments, including proposed solutions, associated with planning for Facilities loaded between 95% and 100% of their applicable Ratings per the criteria in paragraphs (a) and (e), above, and lines 1 and 4 of Table 1 below, shall be completed by no later than May 1, 2015.

| Initial Condition | Event | Maximum Loading (% of Applicable Rating) | No Cascading or Uncontrolled Outages | Non-consequential Load Loss Allowed |
| --- | --- | --- | --- | --- |
| 1 | Normal System | Common tower outage | 95% | Yes | No |
| 2 | Unavailability of a generating unit, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Transmission circuit; or 2. Transformer | 100% | Yes | No |
| 3 | Unavailability of a 345/138 kV transformer, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; or 5. FACTS device | 95% | Yes | No |
| 4 | Normal System | Contingency Loss of one of the following: 1. Transmission circuit; or 2. Transformer | 95% | Yes | No |

Table 1: ERCOT-specific Reliability Performance Criteria

(2)	ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  If a Transmission Facility improvement is required to meet the criteria in this Section 4.1.1.2, but the improvement cannot be implemented in time to resolve the performance deficiency, an interim solution may be used to resolve the deficiency until the improvement has been implemented.