| NOGRR Number | 110 | NOGRR Title | Synchronization with NPRR529, Congestion Management Plan |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | June 19, 2013 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.5.1, Criteria for Removing Contingencies from the Reliability Unit Commitment Analyses 3.7.2, Responsibility for Equipment Ratings 4.3.1, Remedial Action Plans 4.3.2, Real-Time and Short Term Planning 6.2.2, Design and Operating Requirements for ERCOT System Facilities 11, Congestion Management Plans and Special Protection Systems (new) 11.1, Introduction (new) 11.2, Special Protection System (new) 11.2.1, Reporting of SPS Operations (new) 11.3, Remedial Action Plan (new) 11.3.1, RAPs Submitted by Market Participants (new) 11.4, Mitigation Plan (new) 11.5, Pre-contingency Action Plans (new) 11.6, Transmission Outage Action Plan (new) |  |  |
| Protocol Sections Requiring Revision |  | 2.1, Definitions 2.2, Acronyms and Abbreviations 3.1.6.5, Evaluation of Proposed Resource Outage 3.10.7.4, Definition of Special Protection Systems and Remedial Action Plans 6.5.7.1.10, Network Security Analysis Processor and Security Violation Alarm |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) synchronizes the Nodal Operating Guide with revisions proposed by Nodal Protocol Revision Request (NPRR) 529, Congestion Management Plan, and also: - Moves language related to Special Protection Systems (SPSs) and Remedial Action Plans (RAPs) to new Section 11. - Formalizes two existing Congestion Management Plans (CMPs), Transmission Outage Action Plans (TOAPs) and Pre-Contingency Action Plans (PCAPs). - Eliminates the distinction between Type I and Type II SPSs. - Institutes a stakeholder comment process for RAPs that are proposed by Market Participants to provide for input from other Market Participants into ERCOT’s approval process for these Market Participant-proposed RAPs. |  |  |
| Reason for Revision |  | To provide clarity and transparency into existing activities. |  |  |
| Procedural History |  | - On 3/6/13, NOGRR110 and an Impact Analysis were posted. - On 4/8/13, Calpine comments were posted. - On 4/17/13, the Operations Working Group (OWG) considered NOGRR110. - On 5/15/13, ERCOT comments were posted. - On 5/15/13, OWG again considered NOGRR110. - On 6/17/13, CenterPoint Energy comments were posted. - On 6/19/13, OWG again considered NOGRR110. |  |  |
| OWG Decision |  | On 4/17/13, OWG was in consensus to table NOGRR110 until after the May 6, 2013 NPRR528, NPRR529 & NOGRR110 Workshop. On 5/15/13, OWG was in consensus to table NOGRR110 for one month. On 6/19/13, OWG was in consensus to table NOGRR110 until the 6/27/13 OWG meeting. |  |  |
| Summary of OWG Discussion |  | On 4/17/13, participants discussed the order in which actions under a CMP will be implemented; whether the definitions proposed by NPRR529 align with NOGRR110; whether ERCOT should be required to issue a Market Notice any time a RAP is submitted; and the length of time an SPS is expected to remain in service after approval. It was requested that ERCOT schedule a workshop to discuss NPRR529, NOGRR110, and NPRR528, Clarification of Assessment of Chronic Congestion, to provide additional clarification. On 5/15/13, it was requested that NOGRR110 be tabled until the June 2013 OWG meeting to allow time for interested parties to review the 5/15/13 ERCOT comments. On 6/19/13, the 6/17/13 CenterPoint Energy comments were reviewed. There was a request for NOGRR110 to be tabled to allow time for additional review. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | - To provide additional clarity around current activities. |
|  | 2 | - The addition of a comment process for RAPs that are proposed by Market Participants should allow for improved transparency and help ensure that any RAPs that are approved through this process are non-discriminatory. |

| Sponsor |  |
| --- | --- |
| Name | Chad Thompson |
| E-mail Address | cthompson@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6508 |
| Cell Number |  |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Calpine 040813 | Proposed revisions to remove a duplicate reporting requirement related to SPS operations, to revise the acronym of Transmission Operator (TO) to “TOP,” and to allow Resource Entities to submit requests for Mitigation Plans, and requested examples of SPS and RAP designs, with focus on what differentiates them from each other. |
| ERCOT 051513 | Proposed revisions based on the discussion at the May 6, 2013 ERCOT NPRR528, NPRR529, and NOGRR110 Workshop. |
| CenterPoint Energy 061713 | Proposed revisions that would allow post contingency flows below the Emergency Rating to avoid unnecessary Load shed, make ERCOT responsible for SPS equipment owned by Generation Resources, and require ERCOT to issue Market Notice for new or modified CMPs. |

Comments

Please note that the baseline Operating Guide language in Section 6.2.2 has been updated due to the incorporation of NOGRR107, Disturbance Monitoring Requirements Clarifications, in the June 1, 2013 Nodal Operating Guides.

Proposed Guide Language Revision

2.5.1	Criteria for Removing Contingencies from the Reliability Unit Commitment Analyses

ERCOT shall remove contingencies from the Reliability Unit Commitment (RUC) analysis when:

(a)	The contingency is known to produce post-contingency results that are incorrect; or

(b)	The contingency is known to produce a non-convergent contingency result which may cause the RUC processes to fail.

3.7.2	Responsibility for Equipment Ratings

(1)	TSPs and Resource Entity owners of Transmission Facilities are responsible for determining the Ratings of their Facilities and shall send the methodology used to ERCOT in accordance with paragraph (3) of Protocol Section 3.10, Network Operations Modeling and Telemetry.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs and Resource Entity owners of Transmission Facilities shall provide to ERCOT all nominal Transmission Element Ratings.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these Ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If an approved Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency, ERCOT shall control the post contingency loading of the Transmission Element to levels below the Emergency Rating.

(c)	If an approved RAP is available, ERCOT shall control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The RAP shall be implemented in a manner such that the RAP post implementation loading will be at, or below, the Normal Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Elements to within Normal Ratings as soon as practicable, based on Good Utility Practice.

- 4.3.1

- Real-Time and Short Term Planning

ERCOT will conduct Real-Time and short term planning based on the security criteria established in the Protocols and these Operating Guides.  Operations during Forced and Planned Outages will also follow these criteria.  Line Ratings are provided to ERCOT in accordance with Protocols and these Operating Guides.  ERCOT will employ Congestion Management Plans (CMPs) and use of Special Protection Systems (SPSs) to facilitate the use of the ERCOT Transmission Grid while maintaining system security and reliability in accordance with the Protocols, these Operating Guides, and applicable North American Electric Reliability Corporation (NERC) Reliability Standards.  ERCOT will address operating conditions under which the reliability of the ERCOT System is inadequate and no solution is readily apparent in accordance with the Protocols and these Operating Guides.

6.2.2	Design and Operating Requirements for ERCOT System Facilities

(1)	Protective relay systems shall be designed to provide reliability, a combination of dependability and security, so that protective relay systems will perform correctly to remove faulted equipment from the ERCOT System.

(2)	For planned ERCOT System conditions, protective relay systems shall be designed not to trip for swings which do not exceed the steady-state stability limit (note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered).  Protective relay systems shall not interfere with the operation of the ERCOT System under the procedures identified in the other sections of these Operating Guides.

(3)	Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

(4)	The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

(5)	Applicable Institute of Electrical and Electronic Engineers (IEEE)/American National Standards Institute (ANSI) guidelines shall be considered when applying protective relay systems on the ERCOT System.

(6)	The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to these Operating Guides or to accepted IEEE/ANSI practice, then the Facility owners affected shall negotiate a solution.

(7)	The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

(8)	Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with the operating characteristics of any generating equipment protective relay systems or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

(9)	Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and protective relay systems.

(10)	Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Upon ERCOT’s request, within 30 days, Generation Entities shall provide documentation of coordination.

ERCOT Nodal Operating Guides

Section 11:  Congestion Management Plans and

Special Protection Systems

[DATE]

# 11	CONGESTION MANAGEMENT PLANS AND SPECIAL PROTECTION SYSTEMS

11.1.	Introduction

(1)	Potential transmission security violations are generally resolved through the Security-Constrained Economic Dispatch (SCED).  In cases where SCED would otherwise be unable to resolve one or more transmission security violations, ERCOT may implement appropriate Congestion Management Plans (CMPs).  These CMPs include, but are not limited to the following:

(a)	Remedial Action Plans (RAPs);

(b)	Mitigation Plans;

(c)	Pre-Contingency Action Plans (PCAPs); and

(d)	Transmission Outage Action Plans (TOAPs).

(2)	Automated Special Protection Systems (SPSs) may also be implemented in order to allow Generation Resources or Transmission Elements that would otherwise be subject to restrictions to operate to their full Rating.

11.2	Special Protection System

(1)	Special Protection Systems (SPSs) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action, other than the isolation of faulted elements, to provide acceptable ERCOT System performance.  SPS actions include, but are not limited to, changes in Demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable Facility loadings.  An SPS does not include under-frequency or Under-Voltage Load Shedding (UVLS).  An SPS owner can be a Transmission Service Provider (TSP) or Generation Resource.

(2)	In addition to the requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards, SPSs shall also meet the following requirements:

(i)	The SPS owner shall coordinate the design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources, TSPs and Direct Current Ties (DC Ties);

(ii)	The SPS shall be automatically armed when appropriate;

(iii)	The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, a TSP that owns an SPS may provide a Real-Time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one or more of the SPS monitored Facilities exceeds 90% of the flow necessary to arm the SPS.  The cost necessary to provide such status indication shall be allocated as agreed by the TSP owner and the Generation Resource owner;

(iv)	The status indication of any automatic or manual arming/activation or operation of the SPS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owners of any Facility controlled by the SPS;

(v)	When an SPS is removed from service, the SPS owner or its Designated Agent shall immediately notify ERCOT.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS and notify the market via the Market Information System (MIS) Public Area.

(vi)	When an SPS is returned to service, the SPS owner or its Designated Agent shall immediately notify ERCOT.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

(vi)	The SPS owner shall telemeter the status indication of the following items SCADA to ERCOT for incorporation into ERCOT systems:

(A)	Any automatic or manual arming/activation or operation of the SPS;

(B)	The in-service/out-of-service status of the SPS; and

(C)	Any additional related telemetry that already exists pertinent to the monitoring of the SPS (e.g. status indication of communications links between associated SPS equipment and TSP or Generation Resource control center, arming limits of associated SPS equipment).

(2)	The owners of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

(a)	ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS at least every five years as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and shall be posted on the MIS Secure Area.

(b)	The review of a proposed SPS shall be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Network Operations Model Change Request (NOMCR) to ERCOT.

(c)	Existing SPSs that have already undergone at least one review shall remain in service during any subsequent review.  Modifications to existing SPSs may be implemented upon approval by ERCOT.

(d)	The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of Facility controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

(e)	ERCOT review of an SPS shall:

(i)	Identify any conflicts with the Protocols, NERC Reliability Standards, and these Operating Guides;

(ii)	Evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required; and

(iii)	Evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself and without any other system contingency.

(f)	If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within 30 days.

(g)	As part of the ERCOT review and unless judged to be unnecessary by ERCOT, the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and/or the System Protection Working Group (SPWG) shall review the SPS and report any comments, questions, or issues to ERCOT for resolution.  ERCOT may work with the owner(s) of Facilities controlled by the SPS as necessary to address all issues.

(g)	ERCOT shall develop a method to include the SPS in Security-Constrained Economic Dispatch (SCED), Outage coordination, and Reliability Unit Commitment (RUC).

(h)	ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

11.2.1	Reporting of SPS Operations

(1)	SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report in Section 8, Attachment B, Relay Misoperation Report.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

(2)	ERCOT shall report all SPS operations and misoperations to the Texas Reliability Entity (Texas RE) for review.  SPS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to the Texas RE.  An operation and misoperation of an SPS with respect to reporting requirements to the Texas RE occurs when changes to the transmission system occur, including, but not limited to circuit breaker operation.  Owners of SPSs will provide a monthly report to ERCOT by the 15th of each month, for the previous month, describing each instance an SPS armed/activated and reset.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to the Texas RE.

(3)	If an SPS which removes generation from service, operates more than two times within a six month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

(4)	For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the MIS Secure Area.  Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, whenever the SPS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all facilities controlled by the SPS.

11.3	Remedial Action Plan

(1)	As defined by Protocols, a Remedial Action Plan (RAP) is a set of pre-defined action executed post-contingency to reduce loading on one or more Transmission Elements to below their Normal Rating.  RAPs may not include load shedding.  Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for any RAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	RAPs must meet the following requirements:

(a)	Be coordinated and approved by ERCOT and all Transmission Operators (TOs) and Resource Entities included in the RAP;

(b)	Limit use to the time required to construct replacement Transmission Facilities; however, the RAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all applicable requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO and Resource Entity actions;

(e)	Include the option for the TO and Resource Entity to override the procedures if the RAP will not improve reliability of the ERCOT System;

(f)	Must not be overly complex and must be able to resolve the issue for which it was designed over the range of conditions that might reasonably be experienced;

(g)	TO and/or Resource Entity must be prepared to execute the RAP;

(h)	An approved RAP must have a 15-minute Rating greater than the Normal and Emergency Ratings for the element or elements it intends to resolve; and

(i)	Be defined in the Network Operations Model and considered in the Security-Constrained Economic Dispatch (SCED) and Reliability Unit Commitment (RUC).  RAPs that cannot be modeled using ERCOT’s existing infrastructure shall be rejected unless the Technical Advisory Committee (TAC) approves a plan to work around the infrastructure problem.

(3)	An approved RAP may be executed immediately, post-contingency, by the TO or Resource Entity without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	When a RAP is removed from service, the TO and or Resource Entity shall immediately notify ERCOT and any other impacted TO and or Resource Entity.  ERCOT shall modify its reliability constraints to recognize the unavailability of the RAP.

(5)	ERCOT shall conduct a review of each existing RAP annually or as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures.

11.3.1	RAPs Submitted by Market Participants

(1)	RAPs may be proposed by any Market Participant or may be developed by ERCOT.

(2)	ERCOT shall post RAPs submitted by a Market Participant not registered as a TSP on the MIS Secure Area within five Business Days of receipt.

(3)	ERCOT shall provide a five Business Day comment period from the date when the proposed RAP under review is posted by ERCOT unless Notice of a shortened comment period is provided.

(4)	ERCOT shall consider all comments received within the five Business Day comment period on the proposed RAP, along with its own evaluation and those of the Transmission Facility owners, and either approve, modify or reject that proposed RAP.

(5)	If a proposed RAP is modified or rejected, ERCOT shall post an explanation for the rejection or a description of the modification.

(6)	ERCOT shall post all approved RAPs on the Market Information System (MIS) Secure Area at least two Business Days prior to implementation and shall specify the date the RAP is scheduled to be implemented.

11.4	Mitigation Plan

- As defined by Protocols, a Mitigation Plan is a set of pre-defined actions executed post-contingency to reduce overloading on one or more Transmission Elements to below their Normal Rating.  Mitigation Plans may include load shedding.  Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for a Mitigation Plan; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	A Mitigation Plan may be proposed by any TSP, but must be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  Mitigation Plans must meet the following requirements:

(a)	Be coordinated with the TOs included in the Mitigation Plan;

(b)	Limited in use to the time required to construct replacement Transmission Facilities;  however, the Mitigation Plan will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Include the option for the TO to override the Mitigation Plan if it will not improve system reliability;

(f)	TOs must be prepared to execute the Mitigation Plan;

(g)	Be able to be implemented in a timeframe that will not result in loss of the overloaded Transmission Element;

(h)  	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the Mitigation Plan in advance or as soon as practicable when developing the Mitigation Plan in Real-Time; and

(i)  	Not subject ERCOT to unacceptable risk of widespread cascading Outages.

(3)	An approved Mitigation Plan may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT shall post approved Mitigation Plans on the Market Information System (MIS) Secure Area.

(5)	Restoration of any Load shed by executing the Mitigation Plan shall be coordinated with ERCOT.

11.5	Pre-Contingency Action Plans

- As defined by Protocols, a Pre-Contingency Action Plan (PCAP) is a set of pre-defined actions executed pre-contingency to reduce overloading on one or more Transmission Elements to below their Normal Rating.  Normally, it is desirable that a Transmission Service Provider (TSP) construct Transmission Facilities adequate to eliminate the need for any PCAP; however, in some circumstances, such construction may be unachievable in the available time frame

(2)	A PCAP may be proposed by any TSP, but must be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  PCAPs must meet the following requirements:

(a)	Be coordinated with the TOs included in the PCAP;

(b)	Limited in use to the time required to construct replacement Transmission Facilities;  however, the PCAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Include the option for the TO to override the PCAP if it will not improve system reliability; and

(f)	TOs must be prepared to execute PCAPs.

(3)	An approved PCAP may be executed immediately, pre-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT shall post approved PCAPs on the Market Information System (MIS) Secure Area.

(5)	ERCOT may limit the quantity of PCAPs that are used.

11.6	Transmission Outage Action Plan

(1)	A Transmission Outage Action Plan (TOAP) is a set of pre-defined actions to executed, post-contingency, during a specified Transmission Facility or Resource Outage, in order to reduce overloading on one or more Transmission Elements to below their Normal Rating.  TOAPs may include load shedding.

(2)	A TOAP may be proposed by a Transmission Service Provider (TSP), but should be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  TOAPs must meet the following requirements:

(a)	Be coordinated with the TOs included in the TOAP;

(b)	Limit use to the duration of a specific Transmission Element or Resource Outage;

(c)	Comply with all requirements of  the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Include the option for the TO to override the TOAP if it will not improve system reliability;

(f)	TOs must be prepared to execute TOAPs;

(g)	Shall be implemented in a timeframe that will not result in loss of the overloaded Transmission Element;

(h)  	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the TOAP in advance or as soon as practicable when developing the TOAP in Real-Time; and

(i)  	Not subject ERCOT to unacceptable risk of widespread cascading Outages.

(3)	An approved TOAP may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT shall post approved TOAPs that will be used for a period greater than 5 operating days on the Market Information System (MIS) Secure Area.

(5)	ERCOT may limit the quantity of TOAPs that are used.

(6)	Restoration of any Load shed by executing the TOAP shall be coordinated with ERCOT.