| NOGRR Number | 111 | NOGRR Title | Synchronization with NPRR527, Required Combined Cycle Telemetry for Operational Awareness and PDCWG Analysis |
| --- | --- | --- | --- |

| Date | July 2, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | David Kee on behalf of the Performance Disturbance Compliance Working Group (PDCWG) |
| E-mail Address | dekee@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | (210) 353-6912 |
| Cell Number | (210) 667-5206 |
| Market Segment | Not applicable. |

Comments

At its June 24, 2013, meeting, the PDCWG reviewed NOGRR111.  After review, the PDCWG was in consensus to endorse the 4/8/13 Calpine comments as revised by PDCWG.

These comments amended the following:

- References to “Generation Resources” were changed to “Resources”;

- Added language to accurately capture the practice of not evaluating Resources within 5MW or 2% of HSL, whichever is larger; and

- Removed references to the summary as it referred to the QSE summary.  The QSE summary is no longer evaluated by the group.  Instead Resources are evaluated individually.

Revised Proposed Guide Language

- 2.2.8	Performance/Disturbance/Compliance Analysis

(1)	Performance/Disturbance/Compliance analysis shall be performed by ERCOT for the purpose of ensuring conformance with the Protocols.  All Resources must respond to frequency disturbances with a Governor droop of 5% or less unless operating within the larger of 5MW or 2% of the Resource’s High Sustained Limit (HSL) for low frequency disturbances or Low Sustained Limit (LSL) for high frequency disturbances or carrying spinning capability only comprised of non-frequency responsive power augmentation equipment.

(2)	ERCOT shall make a regular report on selected system disturbances, documenting the response of individual  Resources.  In addition, Resource Entities, QSEs, and individual members of the Performance Disturbance Compliance Working Group (PDCWG) are encouraged to work within their respective companies to enhance the performance of individual  Resource control systems through application of the results of the PDCWG studies.