ERCOT Operations Report

June 2013 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 6/6/2013 5:13 | 59.897 | 2 | Unit trip with approximately 441 MW net. |
| 6/7/2013 11:53 | 59.894 | 20 | Gen deviation of approximately -83MW during freq event. |
| 6/11/2013 10:56 | 59.828 | 100 | Unit trip with approximately 911 MW net. |
| 6/12/2013 19:45 | 59.832 | 64 | Unit trip with approximately 825 MW net. |
| 6/26/2013 23:09 | 59.866 | 14 | Unit trip with approximately 808 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 6/04/2013 18:04:20 | Unit Trip | Approx. 53 sec | The event was caused by the loss of one unit. The unit was generating 607 MW net before the trip, the frequency dropped to 59.91 Hz. The oscillating frequency of 0.5 Hz with 1.94% damping ratio was observed. |
| 6/11/2013 10:56:30 | Unit Trip | Approx. 60 sec | The event was caused by the loss of one unit. The unit was generating approximately 911 MW net before the trip, the frequency dropped to 59.827 Hz. The oscillating frequency of 0.12 Hz with 3.2% damping ratio was observed. |
| 6/12/2013 19:45:27 | Unit Trip | Approx. 290 sec | The event was caused by the loss of one unit. The unit was generating approximately 825 MW net before the trip, the frequency dropped to 59.836 Hz. The oscillating frequency of 1.00 Hz with 6.0% damping ratio was observed. |
| 6/17/2013 22:57:47 | Unit Trip | Approx. 42 sec | The event was caused by the loss of three units at a single plant. The units were generating approximately 489 MW net before the trip, the frequency dropped to 59.902 Hz. The oscillating frequency of 0.43 Hz with 4.57% damping ratio was observed. |
| 6/25/2013 18:47:39 | Unit Trip | Approx. 31 sec | The event was caused by the loss of one unit. The unit was generating approximately 451 MW net before the trip, the frequency dropped to 59.92 Hz. Two oscillating frequencies of 0.42 Hz with 12.5% damping ratio and 0.61 Hz with 10.5% damping ratio were observed. |
| 6/26/2013 23:09:52 | Unit Trip | Approx. 126 sec | The event was caused by the loss of one unit. The unit was generating approximately 808 MW net before the trip, the frequency dropped to 59.86 Hz. Two oscillating frequencies of 0.42 Hz with 11.33% damping ratio and 0.86 Hz with 8.59% damping ratio were observed. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 6/6/13 5:13:14 | 6/6/13 5:16:50 | 0:03:36 | 378.8 |  |
| 6/11/13 10:56:42 | 6/11/13 11:00:26 | 0:03:44 | 314.08 |  |
| 6/12/13 19:45:26 | 6/12/13 19:48:38 | 0:03:12 | 306.08 |  |
| 6/26/13 23:09:58 | 6/26/13 23:12:42 | 0:02:44 | 332.44 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages (*)

| Contingency Description | Overloaded Element | Total |
| --- | --- | --- |
| Midland East - Moss Switch 345kV | Odessa - Odessa North 138kV | 22 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Laquinta - Lobo 138 kV | 17 |
| DCKT Skyline - Calaveras 345kV | Cagnon AXFMR4H 345/138kV | 17 |
| DCKT Fayette Plant 2 - Lytton Springs & Holman Aen 345 kV | Lost Pines Aen - Austrop 345kV | 15 |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345kV | 14 |
| Mcneil Lcra - Gilleland 138kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 14 |
| DCKT Garfield Aen - Hicross Aen & Onion Creek & Pilot Knob 138kV | Austrop - Daffin 138kV | 12 |
| Fort Stockton Plant - Barrilla 138kV | Fort Stockton Switch - Barrilla 69 kV | 12 |
| Meadow - Ph Robinson 345kV | Alvin Tnp - Freeway Park Tnp 138kV | 12 |
| Morgan Creek Ses Axfmr2h (3) 345/138 kV | Morgan Creek Ses Axfmr1h 345/138kV | 11 |
| Asphalt Mines - Uvalde Aep & Odlaw Switchyard 138kV | Hamilton Road - Maverick 138kV | 11 |
| Illinos #4 - Fort Lancaste 138kV | Friend Ranch - Ozona 69kV | 9 |
| South Texas Project STP_G1 & STP_G2 | Lolita - Blessing 138kV | 8 |
| DCKT Lytton Springs - Slauger Lane & Turnersville 138kV | Lytton Springs - Pilot Knob 138kV | 7 |
| Amoco South Foster - Westover 138kV | Moss Switch - Amoco North Cowden Tap 138 kV | 7 |
| DCKT Graham Ses - Long Creek 345kV | Brown Switch - Killeen Switch 345kV (35090) | 5 |
| DCKT Graham Ses - Long Creek 345kV | Orlando - Vernon 138kV | 5 |
| Salem Lcra At3 345/138kV | Fayett 26AT2 345/138kV | 5 |
| DCKT Jewett - Singleton 345kV | Twin Oak Switch - Btu_Jack_Creek 345 KV | 5 |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Rincon - Bonnieview 69kV | 4 |
| Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 4 |
| DCKT Garfiled Aen - Lytton Springs & Austrop 345kV | Austrop - Daffin 138kV | 4 |
| Pearson Switching Station - Lytle 138kV | Lytle Csw - Devine 69kV | 4 |
| Victoria - Coleto Creek 138kV (Coleto_Victor1) | Coleto Creek - Victoria 138kV (Coleto_Victor2) | 4 |
| DCKT Graham Ses - Long Creek 345kV | Brown Switch - Killeen Switch 345kV (35095) | 3 |
| DCKT Singleton - Zenith 345kV | Singleton - Tomball 345kV | 3 |
| Calallen Sub to Lon_hill 69kV | Lon_hill - Robstown_Tap 69kV | 3 |
| DCKT Gabriel - Bell county & Round Rock 138kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 3 |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69kV | 3 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Pearsall Switching Station - Paloduro Sub 138 kV | 2 |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Sinton - Skidmore 69 kV | 2 |
| DCKT Marion - Zorn and Clear Springs 345 KV | McQueeney - Structural Metals Inc 138kV | 2 |
| DCKT Marion - Zorn and Clear Springs 345 KV | Seguin - Seguin West 138 kV | 2 |
| Btu_Atkins - Btu_Dansby 138kV | Btu_North - Btu_Industrial_Park 69kV | 2 |
| Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345kV | 2 |
| Hunt_ln - Cagnon 138kV | Wstside - Merida 138kV | 2 |
| Big Wells - Dilley Switch Aep 138kV | West Batesville - Asherton 138kV | 2 |
| DCKT Trinidad Ses - Watermill Switch & Tri Corner 345kV | Trinidad Ses Axfmr6 (3) 345/138kV | 2 |
| Cedar Hill Switch Axfmr2l (3) 345/138kV | Sherry Switch - Park Row 138KV (6325_C) | 2 |
| DCKT Ph Robinson - Bayou Cogen & Bayway - Bigbay 138kV | Deer Park - Cardiff 138kV | 2 |
| Valero East - Air Liquid Aep 69kV | Koch Up River 138_69A1 138/69 kV | 2 |
| Kiamichi Energy Facility - Kiowa Switch 345kV | Kiamichi Energy Facility - Kiowa Switch 345kV (Kmchi_Kwass2) | 2 |
| Marion 24at2 345/138 KV | Seguin - Seguin West 138 kV | 2 |
| DCKT Gibons Creek - Singleton 345kV | Jewet - Singleton 345kV (260) | 2 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | San Diego - Freer 69 kV | 1 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Lytle Csw - Devine 69kV | 1 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Asherton - Catarina 138kV (Ashert_Catari1) | 1 |
| DCKT Graham Ses - Long Creek 345kV | Cisco - Leon Switch 138kV | 1 |
| DCKT Garfield Aen - Hicross Aen & Onion Creek & Pilot Knob 138kV | Lytton Springs - Pilot Knob 138kV | 1 |
| Illinos #4 - Fort Lancaste 138kV | Ozona Rea - Pandale 69kV | 1 |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Rincon - Bonnieview 69kV | 1 |
| DCKT Singleton - Zenith 345kV | Roans Prairie - Kuykendahl 345kV | 1 |
| DCKT Singleton - Zenith 345kV | Bellville South - Peters 138kV | 1 |
| Basecase | Laquinta - Lobo 138 kV | 1 |
| Lobo 2_345_138_H 345/138 KV | Falfurrias - Cretonio 69kV | 1 |
| Lobo 2_345_138_H 345/138 KV | Asherton - Catarina 138kV (Ashert_Catari1) | 1 |
| Lobo 2_345_138_H 345/138 KV | San Diego - Freer 69 kV | 1 |
| Lobo 2_345_138_H 345/138 KV | Laquinta - Lobo 138 kV | 1 |
| Btu_Atkins - Btu_Dansby 138kV | Btu_Nall_Lane - Btu_Braiacrest 69kV | 1 |
| Long Creek - Sweetwater East Switch 345 kV | Sweetwater East Switch - Abilene Mulberry Creek 345kV | 1 |
| Aspermont Aep - Spur 138KV | Wolfgang - Rotan 69kV | 1 |
| Aspermont Aep - Spur 138KV | Spur 138_69_1 138/69kV | 1 |
| Bosque Switch - Whitney 138 kV | Lake Whitney Tnp - Whitney 138kV | 1 |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney Tnp 138 kV | 1 |
| Snyder - China Grove Switch 138kV | Amoco Tap - Snyder 69kV | 1 |
| Snyder - China Grove Switch 138kV | China Grove Switch - Amoco Tap 69kV | 1 |
| Golden Switch - Sun Switch 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |
| Palmhurst Sub - North Edinburg 138kV | Duke/HEC - Aderhold 138kV | 1 |
| Palmhurst Sub - North Edinburg 138kV | Aderhold Sub - Elsa 138kV | 1 |
| Ph Robinson At3_H (3)345/138kV | Ph Robinson At1 (3) 345/138kV | 1 |
| Friend Ranch - Fort Lancast 138kV | Ozona Rea - Friend Ranch 138kV | 1 |
| Holt Switch - Moss Switch 138kV | Odessa North - North Cowden 69 kV | 1 |
| China Grove Switch - Morgan Creek Ses 138 kV (6220) | China Grove Switch - Morgan Creek Ses 138 KV (6225) | 1 |
| Mesa View Swithc to Fort Lancaster 138kV | Big Lake - Big Lake Phillips Tap 69kV | 1 |
| DCKT Renner Switch - Allen Switch & Plano Tennyson 138kV | Allen Switch - Plano Alma Road 138 kV | 1 |
| DCKT Hackberry - Valley Ranch & Carrollton Northwest 345kV | Dfw D-East 1 - Dfw C-East 138kV | 1 |
| Salem Lcra - Fayette Plant | Fayett 26AT2 345/138kV | 1 |
| North Cowden - Odessa North 69kV | Odessa North - Odessa Basin Switch 69 kV | 1 |
| DCKT Garfiled Aen - Lytton Springs & Austrop 345kV | Austrop - Daffin 138kV | 1 |
| Stanton East - Big Spring Switch 138kV | Stanton East - 1276 Triangle 138kV | 1 |
| DCKT Calaveras - Beck_Rd & Kirby 138 kV | Grandvew - St_Hedwg 138kV | 1 |
| Pawnee Switching Station - San Miguel 1345_138 Kv Switchyards 345kV | Pawnee Switching Station Xf1 345/138 kV | 1 |
| Andrews North - Andrews Switch 69kV | Andrews North - Means 69kV | 1 |
| DCKT Eagle Mountain Ses - Alliance - Roanoke Switch - Parker Switch 345 kV | Eagle Mountain Ses AXFMR2 345/138kV | 1 |
| Moore_Taylor Electric Coop - Trent 69kV | Eskota Switch - Trent 69kV | 1 |
| Midkiff Switch Axfmr1 138/69 kV | Permian Basin Ses - Hackberry Draw Tap 138kV | 1 |
| Crane Arco - Pegasus 138kV | Permian Basin Ses - Hackberry Draw Tap 138kV | 1 |
| Ajo - Rio Hondo 345 KV | North Edinburg Nedin_XC2 345kV | 1 |
| DCKT Bigbay - Bayway & Ph Robinson - Bayou Cogen 138kV | Deer Park - Cardiff 138kV | 1 |
| Koch Up River - Gila 138kV | Whitepoint Reactor1_Sec 138kV | 1 |
| Gail Sub - Lamesa & Willow Valley Switch 138kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |
| Odessa Texas Instruments - Odessa Ehv Switch & Spraberry Switch 138kV | Midland East - Midland Downtown 138kV | 1 |
| DCKT Hutto Switch - Gilleland 138kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 1 |
| Falcon Seaboard - Midland East 345kV | Stanton East - 1276 Triangle 138kV | 1 |
| DCKT Mountain Creek Ses - Cedar Hill Switch 138kV | Cedar Crest Switch - Oak Cliff South 138kV | 1 |
| DCKT Twin Buttes - Brown Switch & San Angelo Red Creek 345kV | Twin Buttes T1H (3) 345/138 kV | 1 |
| Abilene South - Abilene Aileen 138kV | Abilene South - Abilene W Tex Gulf Tap 69kV | 1 |
| Cagnon Axfmr3l-H (3)345/138kV | Cagnon AXFMR4H 345/138kV | 1 |
| Euless - Liggett Switch 138kV | Dfw D-East 1 - Dfw C-East 138kV | 1 |
| Midland East Axfmr1l (3)345/138 kV | Stanton East - 1276 Triangle 138kV | 1 |
| Utopia - Bandera Lcra 69 kV | Uvalde Aep 138_69A1 468/69kV | 1 |
| DCKT W.A. Parish - Obrien 345kV | Meadow - Ph Robinson 345kV | 1 |
| DCKT Mountain Creek Ses - Cedar Crest Switch 138kV | Mountain Creek Ses - Trinity River Authority 138 kV | 1 |
| Live Oak Aep - Sonora 138kV | Live Oak Aep - Eldorado 69kV | 1 |
| Spraberry Switch - Skywest 138kV | Garden City - Glasscock (Oncor) 69kV | 1 |
| Laquinta - Lobo 138 kV | Falfur 138_69A1 138/69kV | 1 |
| Sun Switch - Morgan Creek Ses 138kV | China Grove Switch - Snyder 138 kV | 1 |
| DCKT Cagnon - Calavers & Braunig 345 kV | Five_Pts - Wstside 138kV | 1 |
| DCKT Austrop -Garfield & Zorn 345kV | Austrop - Daffin 138kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 4 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

3 PCAPS Modified:  06/29

Elgin Switch (ELGSW) 138/69kV Auto Transformer

Odessa EHV – Crane LCRA (Pleasant Farms) 138 kV line

Trinidad-Watermill/TriCorner Double-Circuit 345 kV Line (with Trinidad #6 Online)

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Power Operations Bulletin 629 - Transmission and Security Desk V1 Rev23 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Power Operations Bulletin 628 - Shift Supervisor Desk V1 Rev20 |  |  |  |  |  |
| Power Operations Bulletin 627 - Resource Desk V1 Rev22 |  |  |  |  |  |
| Power Operations Bulletin 626 - Reliability Unit Commitment Desk V1 Rev19 |  |  |  |  |  |
| Power Operations Bulletin 625 - Real Time Desk V1 Rev23 |  |  |  |  |  |
| Power Operations Bulletin 624 - DC Tie Desk V1 Rev19 |  |  |  |  |  |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

06/11 13:56	Advisory issued for Voltage Security Assessment Tool (VSAT) & State Estimator not solving for 30 minutes.

Communication Issues

None

## ERCOT peak (Unofficial)

06/27 17:00 64,426 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 | 2.83 |
| March | 2.24 | 2.02 | 3.49 | 2.68 |
| April | 2.47 | 3.55 | 2.78 | 2.81 |
| May | 2.63 | 3.27 | 3.09 | 3.12 |
| June | 2.84 | 2.28 | 2.85 | 2.51 |
| July | 2.39 | 1.63 | 2.85 |  |
| August | 2.29 | 2.28 | 2.96 |  |
| September | 3.14 | 2.70 | 3.43 |  |
| October | 2.37 | 3.51 | 2.99 |  |
| November | 3.46 | 3.38 | 2.90 |  |
| December | 2.60 | 2.99 | 3.47 |  |
| Annual Average | 2.83 | 2.83 | 3.02 | 2.91 |

OCN, Advisory, Watch & Emergency Notices

Capacity

OCN

None

Advisory

| Date | Event |
| --- | --- |
| 6/11/2013 13:56 | ERCOT issued Advisory due to Voltage Security Assessment Tool (VSAT) as well as State Estimator have not solved in the last 30 minutes. |
| 6/29/2013 12:54 | ERCOT issued Advisory due to geomagnetic disturbance storm of K-7 or higher. |

Transmission Watch

None

Watch

None

Emergency Notice

| Date | Event |
| --- | --- |
| 6/29/2013 15:25 | ERCOT issued Emergency Notice due to the post contingency loss of 138kV line West Conoco to Asherton causes low voltage resulting in the curtailment of the Eagle Pass DC Tie. |

Texas RE Event Analysis

None