Dynamics Working Group

Procedural Manual

Revision 8

ROS Approved

(effective December 31, 2013)

TABLE OF CONTENTS

Foreword	5

1	Activities of the DWG	6

2	Administrative Procedures	6

2.1	Membership	6

2.2	Duties of Chair and Vice-Chair	6

2.3	Meetings	6

2.4	Reports to ROS	6

3	Dynamics Data	7

3.1	General	7

3.1.1	Software	7

The current version of the planning software used by the DWG is PSSE version 33.	7

3.1.2	Dynamics Models – General	7

3.1.3	Standard Dynamics Models	7

3.1.3	User-Written Dynamics Models	8

3.1.4	Maintenance of Dynamics Models	8

3.1.5	Dynamics Data for Existing Equipment	8

3.1.6	Dynamics Data for Planned Equipment	8

3.2	Dynamics Data for Equipment Owned by Resource Entities (RE)	9

3.2.1	Dynamics Data Requirements for New Equipment	9

3.2.2	Updates to Existing Dynamics Data	12

3.3	Data for Load Resource	12

3.4	Dynamics Data for Equipment Owned by Transmission-Distribution Service Providers (TDSP)	12

3.4.1	Underfrequency Firm Load Shedding Relay Data (UFLS)	12

3.4.2	Undervoltage Load Shedding Relay Data	13

3.4.3	Protective Relay Data	13

3.4.4	Load Model Data	14

3.4.5	Other Types of Dynamics Data	14

3.4.6	Missing or Problematic Dynamics Data	15

3.4.7	Dynamics Data and Stability Book Storage	15

4	Overview of DWG Activities	16

4.1	Updating Dynamics Data and Flat Starts	16

4.1.1	Schedule for Dynamic Data Updates and Flat Start Cases	16

4.1.2	Dynamics Data Updates	16

4.1.3	Dynamics Data Screening	16

4.1.4	Flat Start Criteria	16

4.2	Post Flat Start Activities	17

4.2.1	Distribution of Flat Start Results and the Dynamics Data Base	17

4.2.2	Stability Book	17

4.3	Other DWG Activities	18

4.3.1	Dynamic Disturbance Recording (DDR) Equipment Annual Review	18

4.3.2	Event Simulation	19

4.3.3	Procedural Manual Revision Guidelines	19

# Foreword

This Procedural Manual is intended for use by the stakeholder members of the Electric Reliability Council of Texas (ERCOT) for the purpose of creating and maintaining the dynamics database and dynamics simulation cases which are used to evaluate the dynamic performance of the ERCOT system.

The majority of ERCOT members utilize Siemens Power Technologies Inc. (PTI) Power System Simulator (PSS/E) software.  Consequently, the various activities in the procedural manual incorporate PTI procedures and nomenclature in describing these activities. Wherever possible, a description of the PTI activity is given so users of software other than PTI may implement similar actions.

# Activities of the DWG

The DWG will perform the following activities:

- DWG prepares the dynamic data set for the ERCOT system from data supplied by equipment owners and load serving entities. ERCOT coordinates the compilation and publication of dynamics data. The dynamics data will be published in the form of a dynamics study cases (flat start cases) as described within these procedures.

- Prepare a Stability Book that documents data used in the flat start cases.

- Perform other activities as directed by ROS.

# Administrative Procedures

## Membership

DWG membership is open to Transmission Service Providers (TSPs).

Each ERCOT area, as defined in the base case, shall have a designated Dynamics Working Group (DWG) member.  Each designated DWG member shall be identified in the DWG members list, and the list will be updated as needed.

Each January, the DWG will nominate a Chair and Vice-Chair to be approved by the Reliability and Operating Subcommittee (ROS).

## Duties of Chair and Vice-Chair

The Chair will coordinate the activities of the DWG and represent the DWG at the ROS Meetings and other working group meetings as required.

The Vice-Chair will support the Chair and fulfill the duties of the Chair in the absence of the Chair.

## Meetings

The DWG will meet at least quarterly. The Chair may coordinate additional meetings as needed to facilities the activities of the DWG.

Agendas and meeting schedules will be published at least two weeks prior to the meeting. The minutes of each meeting will be distributed to DWG members.

## Reports to ROS

Each month, the DWG will provide a written report to the ROS.

# Dynamics Data

## General

### Software

### The current version of the planning software used by the DWG is PSSE version 33.

### Dynamics Models – General

Dynamic models shall be compatible with the software listed in section 3.1.1.

Models should not interfere with the operation of other models.

All associated dynamic models for a given generating unit shall be provided with the same MBASE in accordance with the machine characteristics where the MBASE is typically the generator MVA rating.

Models using bus numbers shall be compatible with the ERCOT bus numbering system, and shall allow the user to determine the bus numbers.

Models shall be capable of adjusting both load flow and dynamic parameters in response to changing network conditions such as the presence of new nearby generation, FACTS devices, etc.

No model shall restrict the DWG from using any integration time-step less than or equal to a ¼ cycle in simulations.1

ERCOT staff shall inform the ERCOT compliance team if any dynamic data has not been made available or is missing.

### Standard Dynamics Models

The use of PSSE Standard dynamics models is preferred when they can accurately represent the dynamic performance of the device being modeled.

A list of all models approved for use in dynamic simulations of the ERCOT system is maintained on the ERCOT Website http://www.ercot.com/content/gridinfo/generation/ResourceMod.zip

### User-Written Dynamics Models

If there is no compatible standard dynamics model(s), accurate/appropriate user written models may be used.  A user written model is any model that is not a standard Siemens PSS/E library model but has been accepted by DWG after being tested for compatibility with the flat start cases.

User-written models shall be accompanied by a user manual that provides a block diagram for the model, a data sheet for model parameters, and appropriate procedures and considerations for using the model in dynamic simulations.

### Maintenance of Dynamics Models

All associated dynamic models for a given generating unit shall be provided with the same MBASE in accordance with the machine characteristics where the MBASE is typically the generator MVA rating.

User-written dynamics models shall be maintained to be compatible with the software listed in section 3.1.1. Maintenance of the models is the responsibility of the facility owner.

### Dynamics Data for Existing Equipment

“As built” data is required for all completed facilities. Unit-specific data shall be reported for generator units installed after 1990. If a permanent new equipment or temporary equipment in place for more than a year is added to the facility then the dynamic model data needs to be re-submitted.

### Dynamics Data for Planned Equipment

The development of future year case data may require an entity to submit the best available information for the planned equipment prior to development of a detailed design. In such cases, estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted. However, the resource owner shall update the model information upon completion of the detailed design and again upon commissioning the equipment.

## Dynamics Data for Equipment Owned by Resource Entities (RE)

### Dynamics Data Requirements for New Equipment

Note: This section addresses the requirements stated in sections R.1.1, R.1.2, and R.1.5 of NERC Standard MOD-013-1.

RE’s are responsible for providing and tuning, including but not limited to, generator, exciter, power system stabilizer, excitation limiters, and governor model parameters.  Although the final responsibility for the submission and the accuracy of the data lies on the RE’s, ERCOT and the DWG will provide voluntary assistance if requested by RE’s to complete parameter tuning and preparing PSS/E model records. ERCOT will serve as the single point of contact to facilitate these activities. If the DWG identifies inappropriate or incomplete dynamics data, the appropriate DWG member will act through ERCOT to resolve discrepancies with the data owner.  The DWG member of the TDSP to which the generator is connected is responsible for incorporating the dynamics data received from the RE into the DWG Flat Start cases during annual updates.

RE shall fulfill interconnection data requirement by completing the corresponding sections of the RARF for their facilities with dynamic models data embedded or attached to their RARF submission.

The following two subsections describe data requirements for two distinct categories of generation facilities:

  - Conventional Generation Facilities Interconnecting More Than 10 MVA of Generation Capacity:

- The RE shall provide all generator dynamics data and associated generator data.  The data must be provided in the form of PSS/E model data sheets and dynamics model records with tuned parameters.

- The model data shall include, at minimum, a generator model, a governor model, an exciter model, and excitation limiter models. If applicable, the RE shall also provide the power system stabilizer model.

- Classical model data is not acceptable.

- Estimated and/or typical model data is not acceptable for units after they are already connected to the ERCOT system.

- In accordance with the SSWG procedural manual, all non self-serve generation connected to the transmission system at 60kV and above with at least 10 MW aggregated at the point of interconnect must be explicitly modeled.  This translates to (1) no lumping of generating units and (2) explicit modeling of each step-up transformer.

- The SSWG manual states that station auxiliary load for generating plants should not be modeled explicitly at the generator bus.  However, explicit modeling of station auxiliary load may be necessary for dynamic simulations.

- All combined cycle steam turbines shall use the CIGRE governor model, as developed by Siemens PTI and implemented by ERCOT.

- All combined cycle gas turbine models shall be compatible with the CIGRE steam turbine model.

  - Non-Conventional (e.g. Wind and Solar) Facilities:

The Resource Entity is responsible for providing and tuning all models and data for their facility. If a Siemens PTI standard model is not appropriate for the facility, the RE shall obtain the most accurate and appropriate model and the associated data for their wind plant from the manufacturer, and supply it to ERCOT and the TDSP to which it is connected, with the legal authority to provide to all transmission providers.  Regardless of the model source, the RE shall provide the following data as applicable to the generator technology:

- Model, data and description of voltage control method.

- Model, data and description of how they will meet ERCOT reactive requirements.

- A one-line diagram of the proposed facility.

- Data for all transformers. The data should include:

  - MVA rating.

  - High and low side rated voltage.

  - Number of taps, and step size.

  - Impedance, including base values if different from rated values listed above.

- Generator data including:

  - Generator manufacturer and model.

  - Rated voltage.

  - Rated MVA.

  - Reactive capability, leading and lagging.

  - Rated MW output.

  - Net MW output.

  - Transient or subtransient reactance, including base values.

  - Transient or subtransient time constant.

  - Total inertia constant, H, of generator, including the shaft and gearbox.

  - Under frequency and under voltage protection settings.

  - Over frequency and over voltage protection settings.

- If the generator can be modeled using a standard Siemens PTI model, state which model applies to the facility.  Include model parameters, instruction on how to set up, and execute analysis.

- If the model is not a standard Siemens PTI model, provide either dynamic model source code for the generator and associated data or dynamic model object code for the machine and associated data.

  - If providing object code, the object code must be updated for PSS/E version changes or as requested by the DWG and/or ERCOT.

  - Models for the generator, system protection, reactive resources, etc., may be embedded into a single source code or be provided separately.

  - Models should not interfere with the operation of other models.

  - A user’s guide for each model shall be provided.

  - Models using bus numbers shall be compatible with the ERCOT bus numbering system, and shall allow the user to determine the bus numbers.

  - Models shall be capable of adjusting both load flow and dynamic parameters in response to changing network conditions such as the presence of new nearby generation, FACTS devices, etc..

  - Number of machines by manufacturer types.

- List any reactive sources such as capacitor banks, STATCOMS, etc. Provide the number of devices, location of the devices, step size, speed of switching, location where voltage is sensed and controlled, control strategy, and voltage limits.  For dynamic reactive devices, provide the appropriate PTI model and data.

- Line data from the point of connection to each generator.  Include:

  - Line type (overhead or underground)

  - Line length

  - Line resistance in ohms/1000 ft

  - Line reactance in ohms/1000 ft

  - Line susceptance in mhos/1000 ft

- Wind turbine models shall account for rotor mass, aerodynamic energy conversion, pitch control.

### Updates to Existing Dynamics Data

Any change in generator dynamics data, associated generator data, or wind farm items listed in section 3.2.1 , or other types of equipment listed in this procedure, determined either through field testing or after changing relevant equipment or equipment settings shall be reported to ERCOT and the TSP to which they are connected, by the RE within 30 days.  Model data shall be provided in the same form (such as PSS/E model data sheets) as required in section 3.2.1. The requirements of section 3.2.1 apply to all updated models and data. Obsolete data should be deleted.  These updates may also be required as needed to perform ERCOT dynamic studies.

As per section 3.1.4., when updated equipment modifications are provided, data for all other related models shall be updated with the same MBASE. Examples of modifications that require an RE to provide updated model data include replacement of an old excitation system with a new excitation system or boiler/turbine upgrades.

## Data for Load Resource

Load Resource models shall be prepared using a PSSE standard model. Data for the Load Resource model shall be documented in the Stability Book and .dyr files posted to the DWG data site.

## Dynamics Data for Equipment Owned by Transmission-Distribution Service Providers (TDSP)

### Underfrequency Firm Load Shedding Relay Data (UFLS)

The DWG shall prepare annually the UFLS data. Each DWG member is responsible for preparing the UFLS relay model records for the loads within their TDSP.  The DWG member shall submit the UFLS relay data to ERCOT in the form of a PSSE dyre file using an appropriate PSSE standard model. The models should contain the necessary information to properly represent the UFLS relay actions in a dynamic study, including:

- Owner and operator of the UFLS program.

- Size and location of customer load, or percent of connected load, to be interrupted.

- Corresponding frequency set points.

- Overall scheme clearing times (includes all time delays, breaker clearing times, etc).

Also, the DWG member of the TDSP should indicate any other schemes that are part of or impact the UFLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UVLS and Special Protection Systems.

All UFLS data will be documented in the annual Stability Book.

### Undervoltage Load Shedding Relay Data

Note: This section addresses requirements stated in NERC Standards PRC-20 and PRC-21.

Annually or after installation of any undervoltage load shedding (UVLS) relays, the TDSP installing the UVLS relays will submit the corresponding PSS/E relay model to the designated DWG member during the annual data update or as needed for DWG studies. The DWG member shall submit the UVLS relay data to ERCOT in the form of a PSSE dyre file using an appropriate PSSE standard model.  The models shall contain the necessary information to properly represent the undervoltage relay actions in a dynamic study, including:

- Owner and operator of the UVLS program.

- Size and location of customer load, or percent of connected load, to be interrupted.

- Corresponding voltage set points.

- Overall scheme clearing times (includes all time delays, breaker clearing times, etc).

Also, the DWG member of the TDSP should indicate any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems.

All UVLS data will be documented in the annual Stability Book.

### Protective Relay Data

The operation of protection, control, and special protection systems can affect the dynamic performance of the ERCOT system during and following contingencies.  Planning, documenting, maintaining, or other activities associated with these systems is outside the scope of the DWG.  However, because they can affect dynamic performance, the DWG should, on an as needed basis, identify and document protection, control, and special protection systems, which affect multiple transmission providers.  Identification activities will normally require the assistance of individuals or groups outside the DWG.  The specific information to be considered for inclusion will depend on the type, purpose, and scope of study.

Protection, control, and special protection systems included in the DWG database should be in the form of a standard PSS/E model or models.  A descriptive model, such as a time-based sequence of events, is also acceptable.  Protection, control, and special protection systems adequately modeled for dynamic purposes by other working groups only need to be referenced in the DWG study reports.

The DWG member, as part of the annual database update, shall review and update as necessary protection, control, and special protection systems already in the DWG database.  This review should include evaluating the existing data for applicability and accuracy.

Protective relay data included in a DWG flat start case shall be documented in the Stability Book.

### Load Model Data

Note: This section addresses the requirements stated in NERC Standard MOD-013-1 (R1.4).

Another key component of any dynamic study is the load model and its representation as a function of changing frequency or voltage.  The load model can have a significant effect on results of dynamic analysis.  For this reason, it is important to consider the load model and to use an appropriate model during the study.  The DWG will document, in a table in the annual Stability Book, standard load models for each area, composed of a mix of constant impedance, constant current, and constant power generally used in studies.  A standard load-frequency dependency model (LDFRAL) will also be documented in the Stability Book.

Each study performed by the DWG, ERCOT, or by TDSP members submitted to an ERCOT regional planning group should document the load modeling assumptions in the body of the report.

### Other Types of Dynamics Data

Note: This section addresses requirements stated in NERC Standards MOD-013-1 (R1.3).

After a dynamic element planned to be installed on the transmission system owned by a TDSP is modeled in the SSWG base cases such as an SVC, STATCOM, SMES, DC ties, and Variable-Frequency Transformer data, the DWG member of the TDSP owning the equipment will provide the corresponding PSS/E model to the designated DWG member during the annual dynamic database update or as needed for DWG studies.

### Missing or Problematic Dynamics Data

The DWG is responsible for reviewing the dynamics data on an annual basis or as requested by ROS and reporting to the ROS any missing data or unresolved issues relating to data submission requirements.  If there are any problems with the data, the DWG will work through ERCOT with the equipment owner to resolve the problems. However, the final responsibility for the submission and the accuracy of the data lies with the equipment owner. All of the data and the revisions requested by ERCOT shall be resolved by the entity owning the equipment within 30 days.  Until valid data becomes available, the DWG member to whose system the equipment is connected shall recommend an interim solution to the missing or problematic data.

### Dynamics Data and Stability Book Storage

ERCOT shall make available to the DWG members in electronic format the dynamics data described in this procedure.  It shall maintain a repository of dynamics data approved by the DWG and will maintain the submitted revisions. All of the generator data, associated generator data, and wind farm items listed in section 3.2.1 received by ERCOT shall be forwarded to the DWG member of the TDSP to which the generator is connected within 30 days.  ERCOT staff shall inform the ERCOT compliance team if any data is missing or has not been made available.

# Overview of DWG Activities

## Updating Dynamics Data and Flat Starts

### Schedule for Dynamic Data Updates and Flat Start Cases

Each February, the DWG shall prepare a schedule for updating dynamics data and preparing the DWG flat start cases.

The DWG shall prepare the following flat start cases based on the following SSWG steady state cases:

- Dataset A summer on-peak

- A future year Dataset B summer on-peak case

- The future year Dataset B high wind low load case

The DWG may choose to flat start additional cases.

After January 1st, 2015, ERCOT shall prepare all the flat start cases.

### Dynamics Data Updates

Each DWG member shall review the dynamic data from the prior year for their area and provide necessary updates according to the schedule established in section 4.1.1. The changes in the data must be identified and submitted with the updated data.  The dynamics data has been tuned throughout the years to ensure proper operation of the models.  In the event the original manufacturer’s data may have been modified during this process, the parameters in the ERCOT dynamics database should not be changed to match manufacturer’s data unless it is absolutely certain that the data is correct.  Obsolete data should be deleted. Data for mothballed units shall be retained.

Other revisions of data that should be submitted to the designated DWG member include updates to the load model (CONL), Zsource corrections, generation netting, or any other modifications to the network necessary for dynamic studies.

### Dynamics Data Screening

DWG members should review the dynamics data for equipment connected to their system for completeness and applicability.  The data should be appropriate for the model, and the model should be appropriate for the equipment.  Before submitting data for inclusion in updated dynamics base cases, each DWG member should perform dynamics data screening.  The DWG Dynamic Guidelines provides additional information about modeling and guidelines for screening dynamics data.

### Flat Start Criteria

DWG Flat Start cases shall:

- Initialize with no errors;

- Demonstrate that simulation output channels for frequency, voltage and power do not deviate from an acceptable range for a ten-second run with no disturbance.

- The product of a successful flat start will be a simulation-ready base case (the unconverted base case) with its associated dynamic data files including user models, stability data change documentation, and IDEV files.  The product of a successful flat start also includes the steps taken to build the flat start case such as network model changes (i.e. changing the schedule of the North DC, tuning voltages, etc.).  The DWG Dynamic Guidelines provides additional information regarding guidelines for performing a flat start.

## Post Flat Start Activities

### Distribution of Flat Start Results and the Dynamics Data Base

Upon completion of each flat start, an electronic copy of all dynamics data and final data files will be distributed electronically in PTI format to each of the DWG members and to ERCOT System Planning for archiving.  This dynamic data distribution shall be within the schedule established by the DWG for the given flat start.

### Stability Book

The Stability Book is an annual document used to record dynamics data changes and/or corrections required during the flat start processes.  Recommendations to revise load flow data are also included in the book.  DWG Members are required to communicate these recommendations to their respective SSWG member to eliminate recurring problems.

To verify the successful completion of the flat start process, this book should also contain plots of the flat start results. The plots should include, at a minimum, the six (6) worst units (based on angle deviation).

The dynamics data is also included in the stability book. This data is in the DOCU ALL PTI format.

Also included in the stability book is the load shedding relay data submitted by each of the appropriate DWG members.

Section 3.4 identifies additional information that will be included in the Stability Book.

## Other DWG Activities

### Dynamic Disturbance Recording (DDR) Equipment Annual Review

Note: This section addresses NERC Blackout Recommendation 12b.

The purpose for installing dynamic disturbance recording (DDR) equipment is to:

- Collect actual data following a dynamic disturbance.

- Enable the results of dynamic simulations to be evaluated for effectiveness.

  - Location Requirements:

ERCOT and the DWG shall prepare a list and perform an annual review of facilities that operate above 100 kV, are part of a dynamic stability (not transient stability) interface, and require the installation of a DDR.  ERCOT and the DWG shall forward any revised DDR facility list to the Reliability and Operating Subcommittee (ROS) for its review and approval.  Upon approval of the DDR facility list, facility owners shall have six months to install and place in service DDRs at each listed facility.

DDRs shall be removed or taken out of service by the same process.

  - Data Recording Requirements:

The appropriate quantities, such as the following, must be recorded for equipment operating at 100 kV or above at facilities where DDR equipment is required:

- Bus Voltage

- Line Current

- MW and MVAR flow

- Frequency

  - Triggering Requirements:

DDR equipment triggering should occur for one or more of system voltage magnitude, current magnitude, or frequency magnitude disturbances (V, I, or f) without requiring any circuit breaker operations or trip outputs from protective relay systems.

Disturbance recording equipment shall be capable of continuous recording for not less than 5 minutes and shall be retrievable for a period of not less than 72 hours.

Dynamic Disturbance Recorders (DDR’s) should be time synchronized when practical.

The sampling rate for DDR’s should be 240 samples per second.

  - Data Reporting Requirements:

At DDR installations where communication equipment exists and it is practical, communication from the device should be automatic to an ERCOT central database.  Where communication equipment does not exist or automatic communication from the device to ERCOT is not practical, facility owners who have installed DDR's may report data for any event they consider significant to ERCOT.  ERCOT may request facility owners who have installed DDR's to report data for any event.  ERCOT’s request should be made within 24 hours after the event to allow the transmission provider adequate time to retrieve the data.  DDR data of significant events shall be reported to ERCOT at least annually for compilation into a database.

The database compiled by ERCOT shall be made available to all ERCOT members for verifying and improving system models, or analyzing system disturbances.  Submitted data will be retained by ERCOT for a minimum of one year.

DDR records shall be provided to ERCOT and NERC upon request. Disturbance records shall be retained and made available for at least one year from the date the record was made.  DDR records shall be shared between entities, upon request, for the analysis of system disturbances.

  - Maintenance and Testing Requirements:

DDR equipment must be properly maintained and tested in accordance with the manufacturer’s recommendations.  Maintenance and test records shall be provided to ERCOT upon request within 30 business days.

### Event Simulation

Note: This section addresses NERC blackout recommendation 14.

When requested by ROS, the DWG will simulate an actual disturbance event for the purpose of assessing the fidelity of the ERCOT dynamics models and data with actual system performance during the event. In addition, the DWG will annually consider recent significant events to determine their suitability for an event simulation. The DWG will consider their work load and the type of information likely to be obtained in making a decision as to whether to simulate an event.

### Procedural Manual Revision Guidelines

Note: This section addresses requirements stated in NERC Standards MOD-013-0 (R2).

The DWG is responsible for maintaining and updating this Procedural Manual.  Revisions, additions and/or deletions to this Procedural Manual may be undertaken at such times that the DWG feels it is necessary due to changes in PTI dynamic simulation software or to meet new and/or revised requirements of NERC, ERCOT, or any other organization having oversight or regulatory authority.

At least annually, the DWG Chair shall notify the DWG requesting each member to make a thorough review of the current Procedural Manual for any needed revisions.  The notification will request that proposed revisions be submitted to the DWG Chair (or the Chair’s designate) for consolidation and distribution to all DWG members for comment and/or additional revision.  Depending on the magnitude and nature of the revisions being considered, this review process may require more than one cycle before approval is considered.  The DWG Chair should give consideration to being able to complete the review and revision process in time to avoid any delays in collecting dynamic data or completing other DWG work.

The DWG Chair may seek approval of any revision, addition, or deletion to the Procedural Manual by email vote, regular meeting, or called special meeting as deemed necessary or requested by DWG membership.

1 Siemens PSS/E standard library models allow time constants of less than 1 cycle (0.016667 seconds) but use an internal method so that a ¼ cycle (0.004167 seconds) integration time-step can be used for simulations.  For example, Siemens PSS/E uses an internal integration for models that would normally require less than a ¼ cycle integration time-step.