| NOGRR Number | 110 | NOGRR Title | Synchronization with NPRR529, Congestion Management Plan |
| --- | --- | --- | --- |
| Date |  | June 17, 2013 |  |
| Submitter’s Information |  |  |  |
| Name |  | Ebby John |  |
| E-mail Address |  | ebby.john@centerpointenergy.com |  |
| Company |  | CenterPoint Energy |  |
| Phone Number |  | 713-207-2136 |  |
| Cell Number |  |  |  |
| Market Segment |  | Investor Owned Utility (IOU) |  |

Comments

CenterPoint Energy appreciates the opportunity to provide comments on this important topic.

ERCOT is proposing to delete the last sentence in the existing Section 2.5.1(c).  The Company does not believe that the proposed deletion should be made and recommends that the language not be deleted unless the requirements are provided in another portion of the Protocols or Operating Guides.

Also, in the current language of Section 2.5.1 (b) of the Operating Guides, as well as Section 6.5.7.1.10 (3e) of the Protocols, the term Mitigation Action Plan (MAP) is already used.  CenterPoint suggests the complete term “Mitigation Action Plan” should be used throughout the various documents.

ERCOT is proposing to delete the last sentence in the existing Section 3.7.2(3)(b).  The Company does not believe that the proposed deletion should be made and recommends that the language not be deleted unless the requirements are provided in another portion of the Protocols or Operating Guides.

Additionally, the Company’s suggested language adds operational time frames to the different Congestion Management Plans that relate the operational requirements of Section 3.7.2 (3) to time frames that a Transmission Facility is allowed  to operate at its Emergency Rating. It is CenterPoint Energy’s understanding that ERCOT is operating the system so that pre-contingency flows on Transmission Facilities are below the Normal Rating and Credible Single Contingency flows are below the Emergency Rating.  Should the contingency occur, ERCOT can operate the Transmission Facility for up to two hours at the Emergency Rating after which the flow must be reduced to the Normal Rating.  This design allows ERCOT time to employ market solutions without having to unnecessarily impact market participants.  ERCOT’s proposed language for the various Congestion Management Plans identify that the actions of the plan must reduce loading to the Normal Rating.  We believe this requirement is too severe and could lead to unnecessary firm load shedding if the post contingency flows are below the Emergency Rating.

In Section 11.1(1)(a), there should be a differentiation between Remedial Action Plans (“RAP”) created in real-time and not already modeled in SCED.  CenterPoint Energy has proposed language clarifying that CMPs may include the creation of a RAP that is not already modeled in SCED.

CenterPoint Energy is concerned that the proposed amendments to the new Section 11.2 of the Nodal Operating Guides could have impacts on responsibilities for North American Electric Reliability Corporation (“NERC”) Standards.  There are various NERC Standards that apply to Special Protection Systems (SPS).  However, not all of the NERC Standards are applicable to the owner of the SPS.  For example, IRO-005-1, Reliability Coordination — Current Day Operations; PRC-001-1, System Protection Coordination; and TOP-005-1, Operational Reliability Information, among others, require the registered Transmission Operator (TOP) to monitor the status and the operation of the SPS.  The TOP is required to notify the Reliability Coordinator, in this case ERCOT ISO, of various items in regards to the SPS.  These notifications include, but may not be limited to, the following: the status of the SPS, a change in status of the SPS, the operation of the SPS, a degradation of the SPS, or a failure of the SPS to operate as designed.  CenterPoint Energy is unwilling to be responsible for any NERC requirements regarding SPSs that are owned and operated by other Entities.  Because ERCOT is advocating the ownership of SPS equipment by Generation Resources, ERCOT should be responsible for the NERC TOP responsibilities for such equipment.

ERCOT is proposing language in 11.3(1) to remove the ability to shed load for RAPs. It is CenterPoint Energy’s understanding that an SPS and a RAP only differ in method of control, SPS are done by automatic action whereas a RAP requires operator control.  Section 11.2(1) includes as an SPS action “changes in Demand” while in Section 11.3(1), a RAP would not include the ability for a load shed action.  As CenterPoint Energy discussed in comments for NPRR 529, if the definition of a SPS includes changes in Demand, then the definition of a RAP should likewise include changes in Demand.  Therefore, the definitions in NPRR 529 and in this NOGRR should be consistent for allowing changes in Demand to address an operating issue.  There are other proposed additions or modifications to the proposed language that provides additional oversight by ERCOT of SPSs.

Clarification needs to be provided by ERCOT on the entities that are allowed to submit RAPs, MAPs, and PCAPs.  Section 11.3 does not specify the entities that are allowed to submit a RAP, but it is implied that any entity can submit a RAP.  It appears that a MAP, a PCAP, and a TOAP can only be submitted by a TSP.  See Sections 11.4(2), 11.5(2), and 11.6(2) respectively.

Additionally, CenterPoint Energy request that Market Notices be issued whenever new or modified Congestion Management Plans are issued.

Revised Proposed Guide Language

2.5.1	Criteria for Removing Contingencies from the Reliability Unit Commitment Analyses

ERCOT shall remove contingencies from the Reliability Unit Commitment (RUC) analysis when:

(a)	The contingency is known to produce post-contingency results that are incorrect; or

(b)	The contingency is known to produce a non-convergent contingency result which may cause the RUC processes to fail.  ERCOT shall create a generic constraint if a non-convergent case represents a voltage collapse.

3.7.2	Responsibility for Equipment Ratings

(1)	TSPs and Resource Entity that own Transmission Facilities are responsible for determining the Ratings of their Facilities and shall send the methodology used to ERCOT in accordance with  the Protocols.  Technical limits established for the operation of Transmission Facilities and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs and Resource Entity owners of Transmission Facilities shall provide to ERCOT all nominal Transmission Facility Ratings.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these Ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If an approved Remedial Action Plan (RAP) is unavailable to unload the Transmission Facility post-contingency, ERCOT shall control the post-contingency loading of the Transmission Facility to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If an approved RAP is available, ERCOT shall control the post-contingency loading of the Transmission Facility to levels below the 15-Minute Rating.  The RAP shall be implemented in a manner such that the RAP post-implementation loading will be at, or below, the  Emergency Rating within 15 minutes and at, or below, Normal Rating within two hours.

(d)	ERCOT shall use best efforts to restore all Transmission Facilities to within Normal Ratings as soon as practicable, based on Good Utility Practice.

- 4.3.1

- Real-Time and Short Term Planning

ERCOT will conduct Real-Time and short term planning based on the security criteria established in the Protocols and these Operating Guides.  Operations during Forced and Planned Outages will also follow these criteria.  Line Ratings are provided to ERCOT in accordance with Protocols and these Operating Guides.  ERCOT will employ Congestion Management Plans (CMPs) and use of Special Protection Systems (SPSs) to facilitate the use of the ERCOT Transmission Grid while maintaining system security and reliability in accordance with the Protocols, these Operating Guides, and applicable North American Electric Reliability Corporation (NERC) Reliability Standards.  ERCOT will address operating conditions under which the reliability of the ERCOT System is inadequate and no solution is readily apparent in accordance with the Protocols and these Operating Guides.

6.2.2	Design and Operating Requirements for ERCOT System Facilities

(1)	Protective relay systems shall be designed to provide reliability, a combination of dependability and security, so that protective relay systems will perform correctly to remove faulted equipment from the ERCOT System.

(2)	For planned ERCOT System conditions, protective relay systems shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered.  Protective relay systems shall not interfere with the operation of the ERCOT System under the procedures identified in the other sections of these Operating Guides.

(3)	Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

(4)	The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected facilities may be subjected, even under first-contingency conditions.

(5)	Applicable Institute of Electrical and Electronic Engineers (IEEE)/American National Standards Institute (ANSI) guides shall be considered when applying protective relay systems on the ERCOT System.

(6)	The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to these Operating Guides or to accepted IEEE/ANSI practice, then the facility owners affected shall negotiate a solution.

(7)	All facility owners shall give sufficient advance notice to ERCOT of any changes to their facilities that could require changes in protective relay systems of neighboring facility owners.

(8)	Facility owners’ operations personnel shall be familiar with the purposes and limitations of protective relay systems.

(9)	The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the facility owner to ensure that protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Where redundant protective relay systems are required, separate AC current inputs and separately fused DC control voltages shall be provided with the upgraded protective relay system.  Documentation of the review shall be maintained and supplied by the facility owner to ERCOT or NERC on their request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

(10)	Upon ERCOT’s request, within 30 days, Resource Entities shall provide ERCOT with the operating characteristics of any generator’s equipment protective relay systems or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

(11)	Upon ERCOT’s request, within 30 days, Generation Resources shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and protective relay systems.

(12)	Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Upon ERCOT’s request, within 30 days, Generation Entities shall provide documentation of coordination.

ERCOT Nodal Operating Guides

Section 11:  Congestion Management Plans and

Special Protection Systems

[DATE]

# 11	CONGESTION MANAGEMENT PLANS AND SPECIAL PROTECTION SYSTEMS

11.1.	Introduction

(1)	Congestion Management Plans (CMPs) are a set of pre-defined actions executed in response to system conditions to resolve one or more thermal or non-thermal transmission security violations. CMPs include, but are not limited to the following:

(a)	Remedial Action Plans (RAPs) that are not already modeled in SCED;

(b)	Mitigation Action Plans (MAPs);

(c)	Pre-Contingency Action Plans (PCAPs); and

(d)	Temporary Outage Action Plans (TOAPs).

(2)	When developing CMPs for thermal transmission security violations, ERCOT shall first attempt to utilize the 15-Minute rating of the impacted Transmission Facilities, where available, to develop RAPs such that the transmission system is utilized to the fullest extent.

(3)	Automated Special Protection Systems (SPSs) may also be implemented in order to allow Generation Resources or Transmission Facilities that would otherwise be subject to restrictions to operate to their full Rating.

11.2	Special Protection System

(1)	Special Protection Systems (SPSs) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action, other than the isolation of faulted facilities, to provide acceptable ERCOT System performance.  SPS actions include, but are not limited to, changes in Demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable Facility loadings.  An SPS does not include under-frequency or Under-Voltage Load Shedding (UVLS).  An SPS owner can be a Transmission Service Provider (TSP) or Generation Resource.

(2)	ERCOT ISO shall be responsible for the coordination of the design, monitoring, and reporting the status of SPS systems that are owned by Generation Resources and only affect that Generation Resource’s equipment.

(3)	In addition to the requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards, SPSs shall also meet the following requirements:

(i)	The SPS owner shall coordinate the design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources, TSPs and Direct Current Ties (DC Ties);

(ii)	The SPS shall be automatically armed when appropriate;

(iii)	The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, the SPS owner may provide a Real-Time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one or more of the SPS monitored Facilities exceeds 90% of the flow necessary to arm the SPS.  The cost necessary to provide such status indication shall be the responsibility of the SPS owner;

(iv)	The status indication of any automatic or manual arming/activation or operation of the SPS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owners of any Facility controlled by the SPS;

(v)	When an SPS is removed from service, the SPS owner or its Designated Agent shall immediately notify ERCOT.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS and notify the market via the Market Information System (MIS) Public Area.

(vi)	When an SPS is returned to service, the SPS owner or its Designated Agent shall immediately notify ERCOT.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

(vi)	The SPS owner shall telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems:

(A)	Any automatic or manual arming/activation or operation of the SPS;

(B)	The in-service/out-of-service status of the SPS;

(C)	The status including any degradation or potential failure to operate as expected; and

(D)	Any additional related telemetry that already exists pertinent to the monitoring of the SPS (e.g. status indication of communications links between associated SPS equipment and the owner’s control center, arming limits of associated SPS equipment).

(4)	The owners of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

(a)	ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS at least every five years as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and shall be posted on the MIS Secure Area.

(b)	The review of a proposed SPS shall be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Network Operations Model Change Request (NOMCR) to ERCOT.

(c)	Existing SPSs that have already undergone at least one review shall remain in service during any subsequent review.  Modifications to existing SPSs may be implemented upon approval by ERCOT.

(d)	The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of Facility controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

(e)	ERCOT review of an SPS shall:

(i)	Verify that it complies with the Protocols, NERC Reliability Standards, and these Operating Guides;

(ii)	Evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required; and

(iii)	Evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself and without any other system contingency.

(f)	If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied by ERCOT to NERC on request within 30 days.

(g)	As part of the ERCOT review, the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and/or the System Protection Working Group (SPWG) shall review the SPS and report any comments, questions, or issues to ERCOT for resolution.  ERCOT shall work with the owner(s) of Facilities controlled by the SPS as necessary to address all issues.

(g)	ERCOT shall develop a method for either ERCOT or the owner of the SPS to include the SPS in Security-Constrained Economic Dispatch (SCED), Outage coordination, and Reliability Unit Commitment (RUC).

(h)	ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

11.2.1	Reporting of SPS Operations

(1)	SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report in Section 8, Attachment B, Relay Misoperation Report.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented by ERCOT and the SPS Owner.

(2)	ERCOT shall report all SPS operations and misoperations to the Texas Reliability Entity (Texas RE) for review.  SPS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to the Texas RE.  An operation and misoperation of an SPS with respect to reporting requirements to the Texas RE occurs when changes to the transmission system occur, including, but not limited to circuit breaker operation.  Owners of SPSs will provide a monthly report to ERCOT by the 15th of each month describing each instance an SPS armed/activated and reset during the previous month.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to the Texas RE.

(3)	If an SPS which removes generation from service operates more than two times within a six month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

(4)	For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the MIS Secure Area.  Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, whenever the SPS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all facilities controlled by the SPS.

11.3	Remedial Action Plan

(1)	As defined by Protocols, a Remedial Action Plan (RAP) is a set of pre-defined actions executed post-contingency to reduce loading on one or more Transmission Facilities to below their Normal Rating within two hours.  RAPs are sufficiently dependable to assume they can be executed within 15 minutes on a post-contingency basis without loss of reliability to the interconnected network.  These plans may be relied upon in allowing additional use of the transmission system.    Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for any RAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	RAPs must:

(a)	Be coordinated and approved by ERCOT and all Transmission Operators (TOs) and Resource Entities included in the RAP;

(b)	Be limited to the time required to construct replacement Transmission Facilities; however, the RAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all applicable requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO and Resource Entity actions;

(e)	Include the option for the TO and Resource Entity to override the procedures if the RAP will not improve reliability of the ERCOT System as determined by ERCOT;

(f)	Must be able to resolve the issue for which it was designed over the range of conditions that might reasonably be experienced;

(g)	Be executed by the TO and/or Resource Entity;

(h)	Have a 15-minute Rating greater than the Normal and Emergency Ratings for the Transmission Facilities it intends to resolve; and

(i)	Be defined in the Network Operations Model and considered in the Security-Constrained Economic Dispatch (SCED) and Reliability Unit Commitment (RUC).  RAPs that cannot be modeled using ERCOT’s existing infrastructure shall be rejected unless the Technical Advisory Committee (TAC) approves a plan to work around the infrastructure problem.

(3)	An approved RAP may be executed immediately after a contingency by the TO or Resource Entity without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT must approve removal of a RAP from service.  The TO and/or Resource Entity shall immediately notify ERCOT and any other impacted TO and/or Resource Entity when the RAP is removed from service.  ERCOT shall modify its reliability constraints to recognize the unavailability of the RAP.

(5)	ERCOT shall conduct a review of each existing RAP annually or as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures.

11.3.1	RAPs Submitted by Market Participants

(1)	RAPs may be proposed by any Market Participant or may be developed by ERCOT.

(2)	ERCOT shall provide a five-Business-Day comment period from the date when the proposed RAP under review is posted by ERCOT unless notice of a shorter comment period is provided.

(3)	ERCOT shall consider all comments received within the five-Business-Day comment period on the proposed RAP, along with its own evaluation and those of the Transmission Facility owners, and either approve, modify or reject that proposed RAP.

(4)	If a proposed RAP is modified or rejected, ERCOT shall post an explanation for the rejection or a description of the modification.

(5)	ERCOT shall issue a Market Notice and post all submitted and approved RAPs on the Market Information System (MIS) Secure Area in accordance with Protocol Section 3.10.7.4, Special Protection Systems and Remedial Action Plans.

11.4	Mitigation Action Plan

- As defined by Protocols, a Mitigation Action Plan (MAP) is a set of pre-defined actions executed post-contingency to reduce overloading on one or more Transmission Facilities below their Normal Rating within two hours.  MAPs may include Load-shedding or changes in Demand.  Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for a MAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	A MAP may be proposed by any TSP, but must be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  MAPs must:

(a)	Be coordinated with the TOs included in the MAP;

(b)	Limited in use to the time required to construct replacement Transmission Facilities;  however, the MAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Include the option for the TO to override the MAP if it will not improve system reliability as determined by ERCOT;

(f)	Be executed by TOs;

(g)	Be able to be implemented in a timeframe that will not result in loss of the overloaded Transmission Facility;

(h)  	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the MAP in advance or as soon as practicable when developing the MAP in Real-Time; and

(i)  	Not subject ERCOT to unacceptable risk of widespread cascading Outages as determined by ERCOT.

(3)	An approved MAP may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT shall issue a Market Notice and post approved MAP on the Market Information System (MIS) Secure Area.

(5)	Restoration of any Load shed by executing the MAP shall be coordinated with ERCOT.

11.5	Pre-Contingency Action Plans

- As defined by Protocols, a Pre-Contingency Action Plan (PCAP) is a set of pre-defined actions executed pre-contingency to reduce post-contingency overloading on one or more Transmission Facilities to below their Normal Rating within two hours.  Normally, it is desirable that a Transmission Service Provider (TSP) construct Transmission Facilities adequate to eliminate the need for any PCAP; however, in some circumstances, such construction may be unachievable in the available time frame

(2)	A PCAP may be proposed by any TSP, but must be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  PCAPs must:

(a)	Be coordinated with the TOs included in the PCAP;

(b)	Be limited in use to the time required to construct replacement Transmission Facilities; however, the PCAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Include the option for the TO to override the PCAP if it will not improve system reliability as determined by ERCOT; and

(f)	Be executed by TOs.

(3)	An approved PCAP may be executed immediately prior to a contingency by the TO without instruction by ERCOT, or shall be executed upon direction by ERCOT.

(4)	ERCOT shall issue a Market Notice and post approved PCAPs on the Market Information System (MIS) Secure Area.

(5)	ERCOT may limit the quantity of PCAPs that are used.

11.6	Temporary Outage Action Plan

(1)	A Temporary Outage Action Plan (TOAP) is a set of pre-defined actions to executed, post-contingency, during a specified Transmission Facility or Resource Outage, in order to reduce overloading on one or more Transmission Facilities to below their Normal Rating.  TOAPs may include load shedding.

(2)	A TOAP may be proposed by a Transmission Service Provider (TSP), but should be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  TOAPs must:

(a)	Be coordinated with the TOs included in the TOAP;

(b)	Limit use to the duration of a specific Transmission Facility or Resource Outage;

(c)	Comply with all requirements of  the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Include the option for the TO to override the TOAP if it will not improve system reliability as determined by ERCOT;

(f)	Be executed by TOs;

(g)	Be implemented in a timeframe that will not result in loss of the overloaded Transmission Facility;

(h)  	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the TOAP in advance or as soon as practicable when developing the TOAP in Real-Time; and

(i)  	Not subject ERCOT to unacceptable risk of widespread cascading Outages as determined by ERCOT.

(3)	An approved TOAP may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT shall issue a Market Notice and post approved TOAPs that will be used for a period greater than five Operating Days on the Market Information System (MIS) Secure Area.

(5)	ERCOT may limit the quantity of TOAPs that are used.

(6)	Restoration of any Load shed by executing the TOAP shall be coordinated with ERCOT.