| PGRR Number | 031 | PGRR Title | Implement 95% Facility Rating Limit in the Planning Criteria |
| --- | --- | --- | --- |

| Date | July 17, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Ken Chui |
| E-mail Address | ken.chui@lcra.org |
| Company | LCRA TSC |
| Phone Number | 512-578-4510 |
| Cell Number |  |
| Market Segment | Cooperative |

Comments

The recommended changes are meant to clean up the proposed PGRR language.

Section 4.1.1.2 (c): LCRA TSC recommends changing the 95% of applicable rating on line 3 Table 1 to 100% of applicable rating to ensure consistency with what’s stated in this section.

Section 4.1.1.2 (e):  LCRA TSC recommends that facilities should not be limited to only transmission circuit and transformer but also generator, shunt device, FACTS device.

Revised Proposed Guide Language Revision

- 4.1.1.2	Reliability Performance Criteria

(1)	The following performance criteria (summarized in Table 1, ERCOT-specific Reliability Performance Criteria, below) shall be applicable to planning analyses in the ERCOT Region:

(a)	With all Facilities in their normal state, following a common tower outage, all Facilities shall be within less than or equal to 95% of their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(b)	With any single generating unit unavailable, followed by Manual System Adjustments, followed by a common tower outage or the contingency loss of a transmission circuit or transformer, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(c)	With any single 345/138 kV transformer unavailable, followed by Manual System Adjustments, followed by a common tower outage, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, or FACTS device, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

(d)	Assessments, including proposed solutions, associated with criteria in paragraph (c), above, and line 3 of Table 1 below, shall be completed by no later than May 1, 2015.

(e)	With all Facilities in their normal state, following the contingency loss of a transmission circuit, circuit, shunt device, FACTS device, or transformer, all Facilities shall be less than or equal to 95% of their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(f)	For the conditions described in paragraphs (a) and (e) above, Facilities may be between 95% and 100% of their applicable Ratings if the loading on those Facilities is not expected to significantly change within the six-year planning horizon.  Examples of such Facilities may include transmission circuits that are radial to Generation Resources where the maximum output of the Generation Resources is not expected to increase within the six-year planning horizon and transmission circuits that are radial to Load that is not expected to significantly increase within the six-year planning horizon.

(g)	Assessments, including proposed solutions, associated with criteria in paragraphs (a) and (e), above, and lines 1 and 4 of Table 1 below, shall be completed by no later than December 1, 2015.

| Initial Condition |  | Event | Maximum Loading (% of Applicable Rating) | No Cascading or Uncontrolled Outages | Non-consequential Load Loss Allowed |
| --- | --- | --- | --- | --- | --- |
| 1 | Normal System | Common tower outage | 95% | Yes | No |
| 2 | Unavailability of a generating unit, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Transmission circuit; or 2. Transformer | 100% | Yes | No |
| 3 | Unavailability of a 345/138 kV transformer, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; or 5. FACTS device | 100% | Yes | No |
| 4 | Normal System | Contingency Loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; or 5. FACTS device. | 95% | Yes | No |

Table 1: ERCOT-specific Reliability Performance Criteria

(2)	ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  If a Transmission Facility improvement is required to meet the criteria in this Section 4.1.1.2, but the improvement cannot be implemented in time to resolve the performance deficiency, an interim solution may be used to resolve the deficiency until the improvement has been implemented.