| NPRR Number | 524 | NPRR Title | Resource Limits in Providing Ancillary Service |
| --- | --- | --- | --- |
| Date |  | August 5, 2013 |  |
| Submitter’s Information |  |  |  |
| Name |  | David Kee on behalf of the Performance, Disturbance, Compliance Working Group (PDCWG) |  |
| E-mail Address |  | dekee@cpsenergy.com |  |
| Company |  | CPS Energy |  |
| Phone Number |  | 210-353-6912 |  |
| Cell Number |  | 210-667-5206 |  |
| Market Segment |  | Not applicable |  |

Comments

At the July 31st meeting of the PDCWG the merits and impacts of NPRR 524 were discussed.  The discussion was open to all market participants in order to thoroughly examine the NPRR.  After a thorough discussion of the NPRR’s intent, the group formulated an updated analysis (noted as #3 below).  The updated analysis considers the impacts of the changes proposed in this NPRR.

- The PDCWG was not able to identify a negative impact to reliability as a result of NPRR524.

- The PDCWG did not reach consensus to endorse the NPRR.

Analysis from June 24th meeting:

1.    Previous RRS characteristics (prior to implementation of NPRR434, which changed the limits from 20% to 24% and allowed for an additional 500MW of RRS procurement)

	RRS capacity is 100% immediately & fully frequency responsive

	RRS capacity on a single resource is limited to 20% of HSL

	Procuring 1150MW RRS from frequency responsive resources results in a minimum of 191.70MW/0.1Hz

	This 1150MW of RRS capacity would be deployed by frequency at 59.4Hz.

	Minimum generation capacity to supply RRS procurement:

1150𝑀𝑊/0.20 = 5750𝑀𝑊

Frequency responsiveness from 5% droop

𝟔𝟎𝑯𝒛 ∗ 𝟓% = 𝟑𝑯𝒛 𝐝𝐞𝐯𝐢𝐚𝐭𝐢𝐨𝐧 𝐫𝐞𝐬𝐮𝐥𝐭𝐬 𝐢𝐧 𝐟𝐮𝐥𝐥 𝐫𝐞𝐬𝐩𝐨𝐧𝐬𝐞

Resulting ERCOT system frequency responsiveness from RRS providers:

|  | 5750𝑀𝑊 | = | 1916.67𝑀𝑊 | = | 191.667𝑀𝑊 |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 3𝐻𝑧 |  | 𝐻𝑧 |  | 0.1𝐻𝑧 |  |

2. Current RRS characteristics (after NPRR 434 implementation)

RRS capacity is 100% immediately & fully frequency responsive

RRS capacity on a single resource is limited to 24% of HSL

Procuring 1400MW RRS from frequency responsive resources results in a minimum of 194.44MW/0.1Hz

Minimum generation capacity to supply RRS procurement:

1400𝑀𝑊/0.24 = 5833.33𝑀𝑊

Frequency responsiveness from 5% droop:

𝟔𝟎𝑯𝒛 ∗ 𝟓% = 𝟑𝑯𝒛 𝐝𝐞𝐯𝐢𝐚𝐭𝐢𝐨𝐧 𝐫𝐞𝐬𝐮𝐥𝐭𝐬 𝐢𝐧 𝐟𝐮𝐥𝐥 𝐫𝐞𝐬𝐩𝐨𝐧𝐬𝐞

Resulting frequency responsiveness from RRS providers:

| 5833𝑀𝑊 | = | 1944.44𝑀𝑊 | = | 194.44𝑀𝑊 |
| --- | --- | --- | --- | --- |
| 3𝐻𝑧 |  | 𝐻𝑧 |  | 0.1𝐻𝑧 |

However for 5% droop to deploy 100% capacity, frequency must drop to 59.28Hz

This creates a situation which allows only 23% of the HSL to be fully deployed by frequency before UFLS.

Minimum capacity of generators theoretically able to supply RRS

| 1400𝑀𝑊 | = | 5833.33MW | − | 1%(5833𝑀𝑊) | = | 5774.67𝑀𝑊 |
| --- | --- | --- | --- | --- | --- | --- |
| 0.24 |  |  |  |  |  |  |

Resulting ERCOT system frequency responsiveness from RRS providers:

|  | 𝟓𝟕𝟕𝟒.𝟔𝟕𝑴𝑾 | = | 𝟏𝟗𝟐𝟒.𝟖𝟗𝑴𝑾 | = | 𝟏𝟗𝟐.𝟒𝟗𝑴𝑾 | 𝒂𝒄𝒉𝒊𝒆𝒗𝒂𝒃𝒍𝒆 𝒑𝒓𝒊𝒐𝒓 𝒕𝒐 𝑼𝑭𝑳𝑺 |
| --- | --- | --- | --- | --- | --- | --- |
|  | 𝟑𝑯𝒛 |  | 𝑯𝒛 |  | 𝟎.𝟏𝑯𝒛 |  |

Analysis from July 31st meeting:

3. Proposed RRS characteristics (proposed by NPRR 524)

At a minimum, the first 83% of the full RRS Responsibility from generators must be fully frequency responsive.

RRS capacity on a single resource is limited to 24% of HSL.

Procuring 1400MW RRS from both frequency responsive & non responsive resources results in a minimum of 193.67MW/0.1Hz

Separation of Frequency Responsive and NonFrequency Responsive generation capacity to supply 1400 MW RRS procurement

- Minimum capacity of Frequency Responsive generators able to supply RRS

- Plus NonFrequency Responsive Capacity

- Frequency responsiveness from 5% droop:

𝟔𝟎𝑯𝒛 ∗ 𝟓% = 𝟑𝑯𝒛 𝐝𝐞𝐯𝐢𝐚𝐭𝐢𝐨𝐧 𝐫𝐞𝐬𝐮𝐥𝐭𝐬 𝐢𝐧 𝐟𝐮𝐥𝐥 𝐫𝐞𝐬𝐩𝐨𝐧𝐬𝐞

Resulting ERCOT system frequency responsiveness from RRS providers:

5% droop will deploy 100% of the 1162MW RRS capacity when frequency drops to  59.364Hz

Revised Cover Page Language

No revisions are proposed at this time.

Revised Proposed Protocol Language

No revisions are proposed at this time.