## Slide 1: 2017 Generation Deliverability Analysis
ROS Meeting: August 15, 2013
Jeff Billo
ERCOT Transmission Planning

## Slide 2: Background
At the April 2013 meeting ROS requested that ERCOT analyze transmission constraints that may affect generation deliverability
The problem:
  Transmission constraints may prohibit a generator from being able to deliver their full output under certain conditions
  This is generally considered an acceptable way to operate a power system since it would be inefficient to build a transmission system to allow for all generators to deliver full output for all conditions
  As long as there is other generation on the system that can make up for the curtailed generation this is not a problem
  However, at peak conditions when resource adequacy is low it may be necessary to plan for all generation to be able to reach full output
What is the extent of this problem?

## Slide 3: Methodology for Calculating Non-deliverable Generation
Determine transmission constraints that could potentially limit power transfer from each generation site to the rest of the ERCOT system
Group generators with shared transfer limiters to determine if all units can inject into the system at full MW output without overloading the shared constraint post-contingency (excluding groups which are primarily made up of wind, hydro or strictly self-serve units)
If the most limiting transmission constraint is overloaded post-contingency, determine the minimum generation curtailment needed to relieve the overload

## Slide 4: Methodology for Calculating Non-deliverable Generation
Input Data
  Final 2017 summer case from the 2012 5YTP
    NW and SE cases used based on location of the generator
  Contingency definitions
    NERC B and double circuit contingency definitions submitted by SSWG
    Single elements
Scaling the Case
  Increase MW output of the injection group (all units that share a transmission constraint) to 100% of installed capacity
  Increase the load in the case by the same MW value (distributed throughout the system)
Calculating Non-deliverable Generation
  Simulate the most limiting contingency that causes a thermal overload
  Determine the minimum curtailment necessary to relieve the overload by scaling down the units with the largest shift factors

## Slide 5: Results: 2017 summer peak case
Type | Non-deliverable Generation | Number of Affected Plants
Operational Gas and Coal | 510 MW | 6
Mothball | 669 MW | 4
Private Use Network | 46 MW | 2
Total | 1225 MW | 12

## Slide 6: Questions?