| PGRR Number | 031 | PGRR Title | Implement 95% Facility Rating Limit in the Planning Criteria |
| --- | --- | --- | --- |

| Date | August 20, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Mike Holland |
| E-mail Address | Michael.Holland@oncor.com |
| Company | Oncor |
| Phone Number | (214) 743-6677 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

Comments

Oncor submits these comments to allow for a 36 month period for Transmission Service Providers (TSPs) to evaluate loading between 95% and 100% of applicable Facility Ratings.

Revised Proposed Guide Language

- 4.1.1.2	Reliability Performance Criteria

(1)	The following performance criteria (summarized in Table 1, ERCOT-specific Reliability Performance Criteria, below) shall be applicable to planning analyses in the ERCOT Region:

(a)	With all Facilities in their normal state, following a common tower outage, or following the contingency loss of a transmission circuit or transformer,  all Facilities shall be  within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(i)	For the conditions described in paragraph (1)(a) above, Facilities may be between 95% and 100% of their applicable Ratings if the loading on those Facilities is not expected to significantly change within the six-year planning horizon.  Examples of such Facilities may include transmission circuits that are radial to Generation Resources where the maximum output of the Generation Resources is not expected to increase within the six-year planning horizon and transmission circuits that are radial to Load that is not expected to significantly increase within the six-year planning horizon.

(b)	With any single generating unit unavailable, followed by Manual System Adjustments, followed by a common tower outage or the contingency loss of a transmission circuit or transformer, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(c)	With any single 345/138 kV transformer unavailable, followed by Manual System Adjustments, followed by a common tower outage, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, or FACTS device, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

| Initial Condition |  | Event | Maximum Loading (% of Applicable Rating) | No Cascading or Uncontrolled Outages | Non- Consequential Load Loss Allowed |
| --- | --- | --- | --- | --- | --- |
| 1 | Normal System | Common tower outage; or Contingency loss of one of the following: 1. Transmission circuit; or 2. Transformer | 95% (see paragraph (2)(b) below) | Yes | No |
| 2 | Unavailability of a generating unit, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Transmission circuit; or 2. Transformer | 100% | Yes | No |
| 3 | Unavailability of a 345/138 kV transformer, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; or 5. FACTS device | 100% (see paragraph (2)(b) below) | Yes | No |

Table 1: ERCOT-specific Reliability Performance Criteria

(2)	ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  If a Transmission Facility improvement is required to meet the criteria in this Section 4.1.1.2, but the improvement cannot be implemented in time to resolve the performance deficiency, an interim solution may be used to resolve the deficiency until the improvement has been implemented.

(a)	Assessments, including proposed solutions, associated with criteria in paragraph (1)(c) above, and line 3 of Table 1 above, shall be completed by no later than May 1, 2015.

(b)	Assessments, including proposed solutions, associated with planning for Facilities loaded between 95% and 100% of their applicable Ratings, per the criteria in paragraph (1)(a) above, and line 1 of Table 1 above, shall be completed no later than Minsert date 36 months after Board approval].