## Summary
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2013
Released March 1, 2013
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve forecasted peak demands with expected generation outages in the upcoming spring season (March - May). As such, ERCOT does not anticipate that it will need to declare an Energy Emergency Alert (EEA) during the spring of 2013. While a significant amount of unit maintenance is conducted during the spring season, much of this maintenance is completed prior to the onset of hotter temperatures (and resulting higher electricity demand) in May. However, if record hot weather occurs during the early spring unit maintenance period (March to mid-April), ERCOT could experience an Energy Emergency Alert (EEA) event. An extreme weather event well outside expected conditions could require rotating outages to maintain the integrity of the system as a whole.
ERCOT stakeholder committees are currently reviewing the Effective Load Carrying Capability (ELCC) estimates for wind generation in light of results from the recently concluded Loss-of-Load (LOL) Study for the ERCOT Region. The potential impact of a revision to the current wind ELCC of 8.7% is not included in this seasonal assessment. If the ELCC estimates from the recent LOL Study (14.2% for non-coastal wind generation resources and 32.9% for coastal wind generation resources) were incorporated into this spring assessment, the estimate of available resources would be increased by 925 MW.
Water availability in ERCOT is not expected to pose a threat to generation operations this spring.

## Base and Extreme
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2013
Release Date: March 1, 2013
Forecasted Resources and Demand
|  | Installed Capacity, MW | 64197.447 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Planned Units (not wind) with Signed IA and Air Permit, MW | 0 | Based on in-service dates provided by developers of generation resources
|  | Capacity from Private Networks, MW | 4390 | Based on actual historical net PUN output during non-EEA periods
|  | Switchable Units, MW | 3138 | Installed capacity of units that can switch to other Regions
|  | less Switchable Units Unavailable to ERCOT, MW | -317 | Based on survey responses of Switchable Unit owners
|  | RMR Units to be under Contract, MW | 0
|  | Effective Load-Carrying Capability (ELCC) of Wind Generation, MW | 905.3655 | Based on 8.7% of installed capacity (Effective Load Carrying Capability) of wind per Planning Guide Section 8
|  | ELCC of Planned Wind Units with Signed IA, MW | 59.7777 | Based on in-service dates provided by developers of generation resources
|  | 50% of Non-Synchronous Ties, MW | 553 | Based on 50% of installed capacity of ties, per Planning Guide Section 8
a | Total Resources, MW |  | 72926.5902
b | Peak Demand, MW |  | 58312 | May peak forecast based on average weather conditions over 15 years of weather data
c | Reserve Capacity (a -b), MW |  | 14614.5902
Range of Potential Risks
|  |  | Forecasted Season Peak Load (May) | Peak Maintenance Season (March-April) | Peak Maintenance Season/ Extreme Load
|  | Planned Units (not wind) with Signed IA and Air Permit, MW | -898
|  | Seasonal Load Adjustment |  | -7890 | -2475
|  | Typical Maintenance Outages | 2913 | 2913 | 2913 | Based on average of historic planned outages for May weekdays
|  | Typical Forced Outages | 4458 | 4458 | 4458 | Based on average of historic forced outages for May weekdays
|  | Incremental Unit Outages to Reflect Peak Maintenance Season |  | 8121 | 8121 | Incremental outages based on historic forced and planned maintenance outages for April weekdays
d | Total Uses of Reserve Capacity |  | 6473 | 7602 | 13017
| Capacity Available for Operating Reserves (c-d), MW |  | 8141.5902 | 7012.5902 | 1597.5902
Less than 2,300 MW indicates risk of EEA1

## Inputs for Sensitivities
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2013
Release Date: March 1, 2013
Scenario Inputs
| Forecasted Peak Load for Spring 2013 | 58312 | May peak forecast based on average weather conditions over 15 years of weather data
| Load Adjustment for March - April Peak | -7890 | April peak forecast based on average weather conditions over 15 years of weather data (50,422 MW)
| Load Adjustment for hot April | -2475 | April peak forecast based on 90th percentile weather conditions (55,837 MW)
| Typical Maintenance Outages | 2913 | Based on average of historic planned outages for May weekdays
| Typical Forced Outages | 4458 | Based on average of historic forced outages for May weekdays
| Incremental Outages for Peak Maintenance Season | 8121 | Incremental outages based on historic forced and planned maintenance outages for April weekdays

## Unit Listing
Unit Code | Plant Name | Primary Energy Source | Spring Capacity (MW) | Status
AZ_AZ_G1 | AIRPRO | NG | 42 | Existing
AZ_AZ_G2 | AIRPRO | NG | 42 | Existing
AZ_AZ_G3 | AIRPRO | NG | 42 | Existing | Key to Abbreviations
AZ_AZ_G4 | AIRPRO | NG | 42 | Existing | BIO | Biomass
AMISTAD_AMISTAG1 | AMISTAD | WAT | 37.9 | Existing | BIT | Bituminous Coal
AMISTAD_AMISTAG2 | AMISTAD | WAT | 37.9 | Existing | LFG | Land-fill Gas
APD_APD_PS1 | APPLIED ENERGY | NA | 1 | Existing | LIG | Lignite Coal
HB_DG1 | ATASCOCITA | LFG | 10 | Nonmod | MTE | Methanol
ATKINS_ATKINSG7 | ATKINS | NG | 20 | Existing | MTH | Methane
DG_SPRIN_4UNITS | AUSTIN LANDFILL GAS | UNK | 6 | Nonmod | NG | Natural Gas
AUSTPL_AUSTING1 | AUSTIN PLANT | WAT | 8 | Existing | NUC | Nuclear
AUSTPL_AUSTING2 | AUSTIN PLANT | WAT | 9 | Existing | OG | Other Gas
B_DAVIS_B_DAVIG1 | BARNEY DAVIS | NG | 335 | Existing | OTH | Other
B_DAVIS_B_DAVIG2 | BARNEY DAVIS | NG | 322 | Existing | PC | Pulverized Coal
B_DAVIS_B_DAVIG3 | BARNEY DAVIS | NG | 161 | Existing | SUB | Sub-bituminous Coal
B_DAVIS_B_DAVIG4 | BARNEY DAVIS | NG | 161 | Existing | SUN | Sun (Solar Resource)
BASTEN_GTG1100 | BASTROP ENERGY CENTER | NG | 157 | Existing | UNK | Unknown
BASTEN_GTG2100 | BASTROP ENERGY CENTER | NG | 157 | Existing | WAT | Water (Hydro Resource)
BASTEN_ST0100 | BASTROP ENERGY CENTER | WH | 236 | Existing | WDS | Wood Biomass
TRN_DG1 | BAYTOWN | MTH | 4 | Nonmod | WH | Waste Heat
BBSES_UNIT1 | BIG BROWN SES | LIG | 606 | Existing | WND | Wind
BBSES_UNIT2 | BIG BROWN SES | LIG | 602 | Existing | NA | Unknown
CARBN_BSP_1 | BIG SPRING | WH | 17.5 | Existing
DG_BIOE_2UNITS | BIO ENERGY PARTNERS | NG | 6 | Nonmod
DG_BROOK_1UNIT | BLUE WING SOLAR 1 | SUN | 8 | Nonmod
DG_ELMEN_1UNIT | BLUE WING SOLAR 2 | SUN | 7 | Nonmod
LB_DG1 | BLUEBONNET | LFG | 4 | Nonmod
BOSQUESW_BSQSU_1 | BOSQUE SWITCH | NG | 157 | Existing
BOSQUESW_BSQSU_2 | BOSQUE SWITCH | NG | 157 | Existing
BOSQUESW_BSQSU_3 | BOSQUE SWITCH | NG | 153 | Existing
BOSQUESW_BSQSU_4 | BOSQUE SWITCH | WH | 79 | Existing
BOSQUESW_BSQSU_5 | BOSQUE SWITCH | WH | 209 | Existing
BVE_UNIT1 | BRAZOS VALLEY ENERGY LP | NG | 169 | Existing
BVE_UNIT2 | BRAZOS VALLEY ENERGY LP | NG | 169 | Existing
BVE_UNIT3 | BRAZOS VALLEY ENERGY LP | NG | 270 | Existing
BUCHAN_BUCHANG1 | BUCHANAN | WAT | 16 | Existing
BUCHAN_BUCHANG2 | BUCHANAN | WAT | 16 | Existing
BUCHAN_BUCHANG3 | BUCHANAN | WAT | 17 | Existing
FLCNS_UNIT1 | CAL ENERGY | NG | 77 | Existing
FLCNS_UNIT2 | CAL ENERGY | NG | 77 | Existing
FLCNS_UNIT3 | CAL ENERGY | NG | 71 | Existing
CALAVERS_OWS1 | CALAVERAS | NG | 420 | Existing
CALAVERS_OWS2 | CALAVERAS | NG | 420 | Existing
CALAVERS_JKS1 | CALAVERAS | SUB | 562 | Existing
CALAVERS_JKS2 | CALAVERAS | SUB | 775 | Existing
CALAVERS_JTD1 | CALAVERAS | SUB | 430 | Existing
CALAVERS_JTD2 | CALAVERAS | SUB | 420 | Existing
CANYHY_CANYHYG1 | CANYON | WAT | 6 | Nonmod
CBY4_CT41 | CEDAR BAYOU 4 | NG | 168 | Existing
CBY4_CT42 | CEDAR BAYOU 4 | NG | 168 | Existing
CBY4_ST04 | CEDAR BAYOU 4 | NG | 182 | Existing
CBY_CBY_G1 | CEDAR BAYOU PLANT | NG | 745 | Existing
CBY_CBY_G2 | CEDAR BAYOU PLANT | NG | 749 | Existing
CVC_CVC_G1 | CHANNELVIEW COGEN | NG | 179 | Existing
CVC_CVC_G2 | CHANNELVIEW COGEN | NG | 177 | Existing
CVC_CVC_G3 | CHANNELVIEW COGEN | NG | 180 | Existing
CVC_CVC_G5 | CHANNELVIEW COGEN | NG | 118 | Existing
AV_DG1 | COASTAL PLAINS RDF | LFG | 7 | Nonmod
COLETO_COLETOG1 | COLETO CREEK | SUB | 650 | Existing
CBEC_GT1 | COLORADO BEND ENERGY CENTER | NG | 77 | Existing
CBEC_GT2 | COLORADO BEND ENERGY CENTER | NG | 71 | Existing
CBEC_GT3 | COLORADO BEND ENERGY CENTER | NG | 75 | Existing
CBEC_GT4 | COLORADO BEND ENERGY CENTER | NG | 75 | Existing
CBEC_STG1 | COLORADO BEND ENERGY CENTER | NG | 103 | Existing
CBEC_STG2 | COLORADO BEND ENERGY CENTER | NG | 108 | Existing
CPSES_UNIT1 | COMANCHE PEAK SES | NUC | 1227 | Existing
CPSES_UNIT2 | COMANCHE PEAK SES | NUC | 1214 | Existing
DG_MEDIN_1UNIT | COVEL GARDENS LG POWER STATION | UNK | 10 | Nonmod
DANSBY_DANSBYG1 | DANSBY | NG | 110 | Existing
DANSBY_DANSBYG2 | DANSBY | NG | 48 | Existing
DANSBY_DANSBYG3 | DANSBY | NG | 48 | Existing
DECKER_DPG1 | DECKER POWER PLANT | NG | 320 | Existing
DECKER_DPG2 | DECKER POWER PLANT | NG | 428 | Existing
DECKER_DPGT_1 | DECKER POWER PLANT | NG | 54 | Existing
DECKER_DPGT_2 | DECKER POWER PLANT | NG | 54 | Existing
DECKER_DPGT_3 | DECKER POWER PLANT | NG | 54 | Existing
DECKER_DPGT_4 | DECKER POWER PLANT | NG | 54 | Existing
DCSES_CT10 | DECORDOVA SES CONSTELLATION | NG | 75 | Existing
DCSES_CT20 | DECORDOVA SES CONSTELLATION | NG | 74 | Existing
DCSES_CT30 | DECORDOVA SES CONSTELLATION | NG | 73 | Existing
DCSES_CT40 | DECORDOVA SES CONSTELLATION | NG | 72 | Existing
DDPEC_GT1 | DEER PARK ENERGY CENTER | NG | 188 | Existing
DDPEC_GT2 | DEER PARK ENERGY CENTER | NG | 204 | Existing
DDPEC_GT3 | DEER PARK ENERGY CENTER | NG | 188 | Existing
DDPEC_GT4 | DEER PARK ENERGY CENTER | NG | 204 | Existing
DDPEC_ST1 | DEER PARK ENERGY CENTER | WH | 290 | Existing
DNDAM_DENISOG1 | DENISON DAM | WAT | 40 | Existing
DNDAM_DENISOG2 | DENISON DAM | WAT | 40 | Existing
DG_BIO2_4UNITS | DFW GAS RECOVERY | LFG | 6 | Nonmod
DUKE_DUKE_GT1 | DUKE (NOW HIDALGO) | NG | 143 | Existing
DUKE_DUKE_GT2 | DUKE (NOW HIDALGO) | NG | 143 | Existing
DUKE_DUKE_ST1 | DUKE (NOW HIDALGO) | WH | 172 | Existing
DG_SCHUM_2UNITS | DUNLOP (SCHUMANSVILLE) | WAT | 4 | Nonmod
DG_SOME1_1UNIT | SOMERSET NORTH | SUN | 6 | Nonmod
DG_SOME2_1UNIT | SOMERSET SOUTH | SUN | 5 | Nonmod
EAGLE_HY_EAGLE_HY1 | EAGLE PASS | WAT | 10 | Nonmod
FALCON_FALCONG1 | FALCON PLANT | WAT | 12 | Existing
FALCON_FALCONG2 | FALCON PLANT | WAT | 12 | Existing
FALCON_FALCONG3 | FALCON PLANT | WAT | 12 | Existing
DG_HBR_2UNITS | FARMERS BRANCH LANDFILL | LFG | 6 | Nonmod
FPPYD1_FPP_G1 | FAYETTE PLANT 1 & 2 | SUB | 608 | Existing
FPPYD1_FPP_G2 | FAYETTE PLANT 1 & 2 | SUB | 608 | Existing
FPPYD2_FPP_G3 | FAYETTE PLANT 3 | SUB | 448 | Existing
FERGUS_FERGUSG1 | FERGUSON | NG | 425 | Existing
FRNYPP_GT11 | FORNEY | NG | 166.7 | Existing
FRNYPP_GT12 | FORNEY | NG | 166.7 | Existing
FRNYPP_GT13 | FORNEY | NG | 166.7 | Existing
FRNYPP_GT21 | FORNEY | NG | 166.7 | Existing
FRNYPP_GT22 | FORNEY | NG | 166.7 | Existing
FRNYPP_GT23 | FORNEY | NG | 166.7 | Existing
FRNYPP_ST10 | FORNEY | NG | 402.9 | Existing
FRNYPP_ST20 | FORNEY | NG | 402.9 | Existing
FREC_GT1 | Freestone Energy Center | NG | 156.2 | Existing
FREC_GT2 | Freestone Energy Center | NG | 156.2 | Existing
FREC_GT4 | Freestone Energy Center | NG | 156.46 | Existing
FREC_GT5 | Freestone Energy Center | NG | 156.46 | Existing
FREC_ST3 | Freestone Energy Center | WH | 178.03 | Existing
FREC_ST6 | Freestone Energy Center | WH | 177.11 | Existing
FRONTERA_FRONTEG1 | FRONTERA | NG | 159 | Existing
FRONTERA_FRONTEG2 | FRONTERA | NG | 159 | Existing
FRONTERA_FRONTEG3 | FRONTERA | WH | 184 | Existing
DG_RDLML_1UNIT | FW REGIONAL LFG GENERATION FACILITY | UNK | 2 | Nonmod
DG_LKWDT_2UNITS | GBRA | WAT | 5 | Nonmod
STEAM_ENGINE_1 | GEUS | NG | 8.439 | Existing
STEAM_ENGINE_2 | GEUS | NG | 8.439 | Existing
STEAM_ENGINE_3 | GEUS | NG | 8.439 | Existing
STEAM_STEAM_2 | GEUS | NG | 26 | Existing
STEAM_STEAM_3 | GEUS | NG | 41 | Existing
STEAM1A_STEAM_1 | GEUS | NG | 20 | Existing
GIBCRK_GIB_CRG1 | GIBBONS CREEK | SUB | 470 | Existing
GRSES_UNIT1 | GRAHAM SES | NG | 225 | Existing
GRSES_UNIT2 | GRAHAM SES | NG | 390 | Existing
GBY_GBY_5 | GREENS BAYOU | NG | 406 | Existing
GBY_GBYGT73 | GREENS BAYOU | NG | 54 | Existing
GBY_GBYGT74 | GREENS BAYOU | NG | 54 | Existing
GBY_GBYGT81 | GREENS BAYOU | NG | 54 | Existing
GBY_GBYGT83 | GREENS BAYOU | NG | 64 | Existing
GBY_GBYGT84 | GREENS BAYOU | NG | 58 | Existing
GUADG_GAS1 | GUADALUPE GEN | NG | 167 | Existing
GUADG_GAS2 | GUADALUPE GEN | NG | 168 | Existing
GUADG_GAS3 | GUADALUPE GEN | NG | 166 | Existing
GUADG_GAS4 | GUADALUPE GEN | NG | 168 | Existing
GUADG_STM5 | GUADALUPE GEN | NG | 168 | Existing
GUADG_STM6 | GUADALUPE GEN | NG | 173 | Existing
HLSES_UNIT3 | HANDLEY SES | NG | 395 | Existing
HLSES_UNIT4 | HANDLEY SES | NG | 435 | Existing
HLSES_UNIT5 | HANDLEY SES | NG | 435 | Existing
HAYSEN_HAYSENG1 | HAYS ENERGY | NG | 220 | Existing
HAYSEN_HAYSENG2 | HAYS ENERGY | NG | 220 | Existing
HAYSEN_HAYSENG3 | HAYS ENERGY | NG | 228 | Existing
HAYSEN_HAYSENG4 | HAYS ENERGY | NG | 228 | Existing
INKSDA_INKS_G1 | INKS DAM | WAT | 14 | Existing
JACKCNTY_CT1 | JACK COUNTY PLANT | NG | 150 | Existing
JACKCNTY_CT2 | JACK COUNTY PLANT | NG | 150 | Existing
JCKCNTY2_CT3 | JACK COUNTY PLANT | NG | 150 | Existing
JCKCNTY2_CT4 | JACK COUNTY PLANT | NG | 150 | Existing
JACKCNTY_STG | JACK COUNTY PLANT | WH | 285 | Existing
JCKCNTY2_ST2 | JACK COUNTY PLANT | WH | 285 | Existing
DG_KMASB_1UNIT | KMAYBTO | OG | 0.1 | Nonmod
LH2SES_UNIT2 | LAKE HUBBARD 2 SES | NG | 515 | Existing
LHSES_UNIT1 | LAKE HUBBARD SES | NG | 392 | Existing
LPCCS_CT11 | LAMAR POWER PARTNERS | NG | 161.5 | Existing
LPCCS_CT12 | LAMAR POWER PARTNERS | NG | 161.5 | Existing
LPCCS_CT21 | LAMAR POWER PARTNERS | NG | 161.5 | Existing
LPCCS_CT22 | LAMAR POWER PARTNERS | NG | 161.5 | Existing
LPCCS_UNIT1 | LAMAR POWER PARTNERS | NG | 195 | Existing
LPCCS_UNIT2 | LAMAR POWER PARTNERS | NG | 195 | Existing
LARDVFTN_G4 | LAREDO ENERGY CENTER | NG | 94.2 | Existing
LARDVFTN_G5 | LAREDO ENERGY CENTER | NG | 94.2 | Existing
LEON_CRK_LCPCT1 | LEON CREEK | NG | 48 | Existing
LEON_CRK_LCPCT2 | LEON CREEK | NG | 48 | Existing
LEON_CRK_LCPCT3 | LEON CREEK | NG | 48 | Existing
LEON_CRK_LCPCT4 | LEON CREEK | NG | 48 | Existing
DG_LWSVL_1UNIT | LEWISVILLE | WAT | 22 | Nonmod
LEG_LEG_G1 | LIMESTONE PLANT | LIG | 831 | Existing
LEG_LEG_G2 | LIMESTONE PLANT | LIG | 858 | Existing
LOSTPI_LOSTPGT1 | LOST PINES | NG | 183 | Existing
LOSTPI_LOSTPGT2 | LOST PINES | NG | 175 | Existing
LOSTPI_LOSTPST1 | LOST PINES | NG | 192 | Existing
LFBIO_UNIT1 | LUFKIN BIOMASS | WDS | 53 | Existing
MARBFA_MARBFAG1 | MARBLE FALLS | WAT | 21 | Existing
MARBFA_MARBFAG2 | MARBLE FALLS | WAT | 20 | Existing
MARSFO_MARSFOG1 | MARSHALL FORD | WAT | 36 | Existing
MARSFO_MARSFOG2 | MARSHALL FORD | WAT | 36 | Existing
MARSFO_MARSFOG3 | MARSHALL FORD | WAT | 29 | Existing
MLSES_UNIT1 | MARTIN LAKE SES | LIG | 815 | Existing
MLSES_UNIT2 | MARTIN LAKE SES | LIG | 820 | Existing
MLSES_UNIT3 | MARTIN LAKE SES | LIG | 820 | Existing
DG_MKNSW_2UNITS | MCKINNEY LANDFILL | LFG | 3 | Nonmod
DG_MCQUE_5UNITS | MCQUEENEY (ABBOTT) | WAT | 8 | Nonmod
DG_FREIH_2UNITS | MESQUITE CREEK LANDFILL | LFG | 3 | Nonmod
MDANP_CT1 | MIDLOTHIAN ANP | NG | 220 | Existing
MDANP_CT2 | MIDLOTHIAN ANP | NG | 220 | Existing
MDANP_CT3 | MIDLOTHIAN ANP | NG | 220 | Existing
MDANP_CT4 | MIDLOTHIAN ANP | NG | 220 | Existing
MDANP_CT5 | MIDLOTHIAN ANP | NG | 228 | Existing
MDANP_CT6 | MIDLOTHIAN ANP | NG | 228 | Existing
MIL_MILLERG1 | MILLER | NG | 75 | Existing
MIL_MILLERG2 | MILLER | NG | 120 | Existing
MIL_MILLERG3 | MILLER | NG | 208 | Existing
MIL_MILLERG4 | MILLER | NG | 104 | Existing
MIL_MILLERG5 | MILLER | NG | 104 | Existing
MNSES_UNIT3 | MONTICELLO SES | SUB | 795 | Existing
MGSES_CT1 | MORGAN CREEK SES | NG | 77 | Existing
MGSES_CT2 | MORGAN CREEK SES | NG | 77 | Existing
MGSES_CT3 | MORGAN CREEK SES | NG | 77 | Existing
MGSES_CT4 | MORGAN CREEK SES | NG | 77 | Existing
MGSES_CT5 | MORGAN CREEK SES | NG | 77 | Existing
MGSES_CT6 | MORGAN CREEK SES | NG | 77 | Existing
MCSES_UNIT6 | MOUNTAIN CREEK SES | NG | 121 | Existing
MCSES_UNIT7 | MOUNTAIN CREEK SES | NG | 117 | Existing
MCSES_UNIT8 | MOUNTAIN CREEK SES | NG | 567 | Existing
NEDIN_NEDIN_G1 | N EDINBURG | NG | 213.64 | Existing
NEDIN_NEDIN_G2 | N EDINBURG | NG | 213.64 | Existing
NEDIN_NEDIN_G3 | N EDINBURG | WH | 255.45 | Existing
NACPW_UNIT1 | NACOGDOCHES POWER | WDS | 105 | Existing
NUECES_B_NUECESG7 | NUECES BAY | NG | 322 | Existing
NUECES_B_NUECESG8 | NUECES BAY | NG | 161 | Existing
NUECES_B_NUECESG9 | NUECES BAY | NG | 161 | Existing
OGSES_UNIT1A | OAK GROVE SES | LIG | 840 | Existing
OGSES_UNIT2 | OAK GROVE SES | LIG | 825 | Existing
OECCS_CT11 | ODESSA ECTOR CCS | NG | 156.8 | Existing
OECCS_CT12 | ODESSA ECTOR CCS | NG | 145.8 | Existing
OECCS_CT21 | ODESSA ECTOR CCS | NG | 150.2 | Existing
OECCS_CT22 | ODESSA ECTOR CCS | NG | 147.9 | Existing
OECCS_UNIT1 | ODESSA ECTOR CCS | NG | 216 | Existing
OECCS_UNIT2 | ODESSA ECTOR CCS | NG | 216 | Existing
OKLA_OKLA_G1 | OKLAUNION | BIT | 650 | Existing
OLINGR_OLING_1 | OLINGER | NG | 78 | Existing
OLINGR_OLING_2 | OLINGER | NG | 107 | Existing
OLINGR_OLING_3 | OLINGER | NG | 146 | Existing
OLINGR_OLING_4 | OLINGER | NG | 75 | Existing
PSG_PSG_GT2 | PASGEN | NG | 170 | Existing
PSG_PSG_GT3 | PASGEN | NG | 170 | Existing
PSG_PSG_ST2 | PASGEN | WH | 168 | Existing
PEARSALL_PEARS_1 | PEARSALL | NG | 25 | Existing
PEARSALL_PEARS_2 | PEARSALL | NG | 25 | Existing
PEARSALL_PEARS_3 | PEARSALL | NG | 25 | Existing
PEARSAL2_AGR_A | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PEARSAL2_AGR_B | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PEARSAL2_AGR_C | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PEARSAL2_AGR_D | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PB2SES_CT1 | PERMIAN BASIN SES RELIANT | NG | 69 | Existing
PB2SES_CT2 | PERMIAN BASIN SES RELIANT | NG | 67 | Existing
PB2SES_CT3 | PERMIAN BASIN SES RELIANT | NG | 71 | Existing
PB2SES_CT4 | PERMIAN BASIN SES RELIANT | NG | 72 | Existing
PB2SES_CT5 | PERMIAN BASIN SES RELIANT | NG | 72 | Existing
QALSW_GT1 | QUAIL SWITCH | NG | 80 | Existing
QALSW_GT2 | QUAIL SWITCH | NG | 80 | Existing
QALSW_GT3 | QUAIL SWITCH | NG | 80 | Existing
QALSW_GT4 | QUAIL SWITCH | NG | 80 | Existing
QALSW_STG1 | QUAIL SWITCH | NG | 98 | Existing
QALSW_STG2 | QUAIL SWITCH | NG | 98 | Existing
RIONOG_CT1 | RIO NOGALES POWER PROJECT | NG | 162 | Existing
RIONOG_CT2 | RIO NOGALES POWER PROJECT | NG | 162 | Existing
RIONOG_CT3 | RIO NOGALES POWER PROJECT | NG | 162 | Existing
RIONOG_ST1 | RIO NOGALES POWER PROJECT | WH | 323 | Existing
RAYBURN_RAYBURG1 | SAM RAYBURN SWITCHYD | NG | 13.5 | Existing
RAYBURN_RAYBURG2 | SAM RAYBURN SWITCHYD | NG | 13.5 | Existing
RAYBURN_RAYBURG7 | SAM RAYBURN SWITCHYD | NG | 50 | Existing
RAYBURN_RAYBURG8 | SAM RAYBURN SWITCHYD | NG | 51 | Existing
RAYBURN_RAYBURG9 | SAM RAYBURN SWITCHYD | NG | 50 | Existing
RAYBURN_RAYBURG10 | SAM RAYBURN SWITCHYD | WH | 40 | Existing
SJS_SJS_G1 | SAN JACINTO STEAM | NG | 81 | Existing
SJS_SJS_G2 | SAN JACINTO STEAM | NG | 81 | Existing
SANMIGL_SANMIGG1 | SAN MIGUEL GEN | LIG | 391 | Existing
SANDHSYD_SH_5A | SANDHILL POWER STATION | NG | 159 | Existing
SANDHSYD_SH_5C | SANDHILL POWER STATION | NG | 148 | Existing
SANDHSYD_SH1 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH2 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH3 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH4 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH6 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH7 | SANDHILL POWER STATION | NG | 47 | Existing
SD5SES_UNIT5 | SANDOW 5 SES | LIG | 570 | Existing
SILASRAY_SILAS_10 | SILAS RAY | NG | 48 | Existing
SILASRAY_SILAS_9 | SILAS RAY | NG | 40 | Existing
SILASRAY_SILAS_6 | SILAS RAY | WH | 21 | Existing
GIDEON_GIDEONG1 | SIM GIDEON | NG | 130 | Existing
GIDEON_GIDEONG2 | SIM GIDEON | NG | 133 | Existing
GIDEON_GIDEONG3 | SIM GIDEON | NG | 336 | Existing
DG_FERIS_4UNITS | SKYLINE LANDFILL GAS | UNK | 6 | Nonmod
STP_STP_G1 | SOUTH TEXAS PROJECT | NUC | 1375 | Existing
STP_STP_G2 | SOUTH TEXAS PROJECT | NUC | 1375 | Existing
SPNCER_SPNCE_4 | SPENCER | NG | 61 | Existing
SPNCER_SPNCE_5 | SPENCER | NG | 61 | Existing
SCSES_UNIT1A | STRYKER CREEK SES | NG | 167 | Existing
SCSES_UNIT2 | STRYKER CREEK SES | NG | 502 | Existing
DG_VALL1_1UNIT | SUNEDISON RABEL ROAD | SUN | 10 | Nonmod
DG_VALL2_1UNIT | SUNEDISON VALLEY ROAD | SUN | 10 | Nonmod
TEN_CT1 | TENASKA (BRAZOS) | NG | 163 | Existing
TEN_STG | TENASKA (BRAZOS) | WH | 106 | Existing
TNSKA_GT1 | TENASKA (TXU) | NG | 86 | Existing
TNSKA_GT2 | TENASKA (TXU) | NG | 86 | Existing
TNSKA_STG | TENASKA (TXU) | WH | 87 | Existing
DG_WALZE_4UNITS | TESSMAN ROAD | MTE | 10 | Nonmod
TXCTY_CTA | TEXAS CITY GEN | NG | 100.62 | Existing
TXCTY_CTB | TEXAS CITY GEN | NG | 100.62 | Existing
TXCTY_CTC | TEXAS CITY GEN | NG | 100.62 | Existing
TXCTY_ST | TEXAS CITY GEN | WH | 131.52 | Existing
TGF_TGFGT_1 | TEXAS GULF SULPHUR | NG | 74 | Existing
THW_THWGT_1 | TH WHARTON | NG | 13 | Existing
THW_THWGT31 | TH WHARTON | NG | 57 | Existing
THW_THWGT32 | TH WHARTON | NG | 57 | Existing
THW_THWGT33 | TH WHARTON | NG | 57 | Existing
THW_THWGT34 | TH WHARTON | NG | 57 | Existing
THW_THWGT41 | TH WHARTON | NG | 57 | Existing
THW_THWGT42 | TH WHARTON | NG | 57 | Existing
THW_THWGT43 | TH WHARTON | NG | 57 | Existing
THW_THWGT44 | TH WHARTON | NG | 57 | Existing
THW_THWGT51 | TH WHARTON | NG | 57 | Existing
THW_THWGT52 | TH WHARTON | NG | 57 | Existing
THW_THWGT53 | TH WHARTON | NG | 57 | Existing
THW_THWGT54 | TH WHARTON | NG | 57 | Existing
THW_THWGT55 | TH WHARTON | NG | 57 | Existing
THW_THWGT56 | TH WHARTON | NG | 57 | Existing
THW_THWST_3 | TH WHARTON | NG | 104 | Existing
THW_THWST_4 | TH WHARTON | NG | 104 | Existing
TNP_ONE_TNP_O_1 | TNP ONE PLANT | LIG | 158 | Existing
TNP_ONE_TNP_O_2 | TNP ONE PLANT | LIG | 158 | Existing
ETCCS_CT1 | TRACTEBEL | NG | 240 | Existing
ETCCS_UNIT1 | TRACTEBEL | NG | 124 | Existing
TRSES_UNIT6 | TRINIDAD SES | NG | 226 | Existing
DG_KLBRG_1UNIT | TRINITY OAKS LFG | LFG | 3 | Nonmod
BRAUNIG_AVR1_CT1 | VH BRAUNIG | NG | 155 | Existing
BRAUNIG_AVR1_CT2 | VH BRAUNIG | NG | 155 | Existing
BRAUNIG_VHB1 | VH BRAUNIG | NG | 220 | Existing
BRAUNIG_VHB2 | VH BRAUNIG | NG | 230 | Existing
BRAUNIG_VHB3 | VH BRAUNIG | NG | 412 | Existing
BRAUNIG_VHB6CT5 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_VHB6CT6 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_VHB6CT7 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_VHB6CT8 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_AVR1_ST | VH BRAUNIG | WH | 180 | Existing
VICTORIA_VICTORG6 | VICTORIA | NG | 168 | Existing
VICTORIA_VICTORG5 | VICTORIA | WH | 127 | Existing
WAP_WAP_G5 | WA PARISH | BIT | 659 | Existing
WAP_WAP_G6 | WA PARISH | BIT | 658 | Existing
WAP_WAP_G7 | WA PARISH | BIT | 577 | Existing
WAP_WAP_G8 | WA PARISH | BIT | 610 | Existing
WAP_WAP_G1 | WA PARISH | NG | 169 | Existing
WAP_WAP_G2 | WA PARISH | NG | 169 | Existing
WAP_WAP_G3 | WA PARISH | NG | 258 | Existing
WAP_WAP_G4 | WA PARISH | NG | 552 | Existing
WAP_WAPGT_1 | WA PARISH | NG | 13 | Existing
WEBBER_S_WSP1 | WEBBERVILLE | SUN | 28.5 | Existing
DG_WSTHL_3UNITS | WESTSIDE | LFG | 5 | Nonmod
WND_WHITNEY2 | WHITNEY DAM | WAT | 15 | Existing
WFCOGEN_UNIT1 | WICHITA FALLS COGEN SWITCH | NG | 20 | Existing
WFCOGEN_UNIT2 | WICHITA FALLS COGEN SWITCH | NG | 20 | Existing
WFCOGEN_UNIT3 | WICHITA FALLS COGEN SWITCH | NG | 20 | Existing
WFCOGEN_UNIT4 | WICHITA FALLS COGEN SWITCH | WH | 17 | Existing
WIPOPA_WPP_G1 | WINCHESTER POWER PARK | NG | 44 | Existing
WIPOPA_WPP_G2 | WINCHESTER POWER PARK | NG | 44 | Existing
WIPOPA_WPP_G3 | WINCHESTER POWER PARK | NG | 44 | Existing
WIPOPA_WPP_G4 | WINCHESTER POWER PARK | NG | 44 | Existing
WIRTZ_WIRTZ_G1 | WIRTZ | WAT | 29 | Existing
WIRTZ_WIRTZ_G2 | WIRTZ | WAT | 29 | Existing
WCPP_CT1 | WISE COUNTY POWER PLANT | NG | 212 | Existing
WCPP_CT2 | WISE COUNTY POWER PLANT | NG | 212 | Existing
WCPP_ST1 | WISE COUNTY POWER PLANT | NG | 241 | Existing
WHCCS_CT1 | WOLF HOLLOW GEN | NG | 227 | Existing
WHCCS_CT2 | WOLF HOLLOW GEN | NG | 227 | Existing
WHCCS_STG | WOLF HOLLOW GEN | WH | 286 | Existing
NWF_NBS | NoTrees Battery Storage | OTH | 36 | Existing
| Total Existing Resources |  | 64197.447
SCES_UNIT1 | SANDY CREEK | SUB | 898 | New
| Total Planned non-Wind Resources |  | 898
PUN AGGREGATE | PUN OUTPUT TO GRID | OTH | 4390 | PUN
| Total Private Use Networks |  | 4390
FTR_FTR_G1 | FRONTIER | NG | 170 | Switchable
FTR_FTR_G2 | FRONTIER | NG | 170 | Switchable
FTR_FTR_G3 | FRONTIER | NG | 170 | Switchable
KMCHI_1CT101 | KIAMICHI ENERGY FACILITY | NG | 178 | Switchable
KMCHI_1CT201 | KIAMICHI ENERGY FACILITY | NG | 180 | Switchable
KMCHI_2CT101 | KIAMICHI ENERGY FACILITY | NG | 178 | Switchable
KMCHI_2CT201 | KIAMICHI ENERGY FACILITY | NG | 180 | Switchable
TGCCS_CT1 | TENASKA GATEWAY | NG | 162 | Switchable
TGCCS_CT2 | TENASKA GATEWAY | NG | 179 | Switchable
TGCCS_CT3 | TENASKA GATEWAY | NG | 178 | Switchable
FTR_FTR_G4 | FRONTIER | WH | 390 | Switchable
KMCHI_1ST | KIAMICHI ENERGY FACILITY | WH | 307 | Switchable
KMCHI_2ST | KIAMICHI ENERGY FACILITY | WH | 307 | Switchable
TGCCS_UNIT4 | TENASKA GATEWAY | WH | 389 | Switchable
| Total Switchable Resources |  | 3138
[7 empty] | Existing ELCC | Potential ELCC
ANACACHO_ANA | Anacacho Windfarm | WND | 101 | Wind |  |  | 8.787 | 14.342
BRAZ_WND_WND1 | Green Mountain Energy 1 | WND | 99 | Wind |  |  | 8.613 | 14.058
BRAZ_WND_WND2 | Green Mountain Energy 2 | WND | 61 | Wind |  |  | 5.307 | 8.662
BRTSW_BCW1 | Barton Chapel Wind | WND | 120 | Wind |  |  | 10.44 | 17.04
BUFF_GAP_UNIT1 | Buffalo Gap Wind Farm 1 | WND | 121 | Wind |  |  | 10.527 | 17.182
BUFF_GAP_UNIT2_1 | Buffalo Gap Wind Farm 2 | WND | 115.5 | Wind |  |  | 10.0485 | 16.401
BUFF_GAP_UNIT2_2 | Buffalo Gap Wind Farm 2 | WND | 117 | Wind |  |  | 10.179 | 16.614
BUFF_GAP_UNIT3 | Buffalo Gap Wind Farm 3 | WND | 170 | Wind |  |  | 14.79 | 24.14
BULLCRK_WND1 | Bull Creek Wind Plant | WND | 88 | Wind |  |  | 7.656 | 12.496
BULLCRK_WND2 | Bull Creek Wind Plant | WND | 90 | Wind |  |  | 7.83 | 12.78
CAPRIDG4_CR4 | Capricorn Ridge Wind 4 | WND | 113 | Wind |  |  | 9.831 | 16.046
CAPRIDGE_CR1 | Capricorn Ridge Wind 1 | WND | 215 | Wind |  |  | 18.705 | 30.53
CAPRIDGE_CR2 | Capricorn Ridge Wind 3 | WND | 150 | Wind |  |  | 13.05 | 21.3
CAPRIDGE_CR3 | Capricorn Ridge Wind 2 | WND | 186 | Wind |  |  | 16.182 | 26.412
CEDROHIL_CHW1 | Cedro Hill Wind | WND | 150 | Wind |  |  | 13.05 | 21.3
CHAMPION_UNIT1 | Champion Wind Farm | WND | 127 | Wind |  |  | 11.049 | 18.034
CSEC_CSECG1 | Camp Springs 1 | WND | 134 | Wind |  |  | 11.658 | 19.028
CSEC_CSECG2 | Camp Springs 2 | WND | 124 | Wind |  |  | 10.788 | 17.608
DG_ROSC2_1UNIT | TSTC West Texas Wind | WND | 2 | Wind |  |  | 0.174 | 0.284
DG_TURL_UNIT1 | WOLFE FLATS | WND | 1 | Wind |  |  | 0.087 | 0.142
ELB_ELBCREEK | Elbow Creek Wind Project | WND | 119 | Wind |  |  | 10.353 | 16.898
ENAS_ENA1 | Snyder Wind Farm | WND | 63 | Wind |  |  | 5.481 | 8.946
EXGNWTL_WIND_1 | Whitetail Wind Energy Project | WND | 91 | Wind |  |  | 7.917 | 12.922
FLTCK_SSI | Silver Star | WND | 60 | Wind |  |  | 5.22 | 8.52
GOAT_GOATWIN2 | Goat Wind 2 | WND | 70 | Wind |  |  | 6.09 | 9.94
GOAT_GOATWIND | Goat Wind | WND | 80 | Wind |  |  | 6.96 | 11.36
HHGT_CALLAHAN | Horse Hollow Wind Callahan | WND | 114 | Wind |  |  | 9.918 | 16.188
HHGT_HHOLLOW1 | Horse Hollow Wind 1 | WND | 213 | Wind |  |  | 18.531 | 30.246
HHGT_HHOLLOW2 | Horse Hollow Wind 2 | WND | 184 | Wind |  |  | 16.008 | 26.128
HHGT_HHOLLOW3 | Horse Hollow Wind 3 | WND | 224 | Wind |  |  | 19.488 | 31.808
HHGT_HHOLLOW4 | Horse Hollow Wind 4 | WND | 115 | Wind |  |  | 10.005 | 16.33
HWF_HWFG1 | Hackberry Wind Farm | WND | 162 | Wind |  |  | 14.094 | 23.004
INDL_INADALE1 | Inadale Wind | WND | 197 | Wind |  |  | 17.139 | 27.974
INDNENR_INDNENR | Desert Sky Wind Farm 1 | WND | 84 | Wind |  |  | 7.308 | 11.928
INDNENR_INDNENR_2 | Desert Sky Wind Farm 2 | WND | 77 | Wind |  |  | 6.699 | 10.934
INDNNWP_INDNNWP | Indian Mesa Wind Farm | WND | 83 | Wind |  |  | 7.221 | 11.786
KEO_KEO_SM1 | Sherbino I | WND | 150 | Wind |  |  | 13.05 | 21.3
KEO_SHRBINO2 | Sherbino 2 | WND | 150 | Wind |  |  | 13.05 | 21.3
KING_NE_KINGNE | King Mountain NE | WND | 79 | Wind |  |  | 6.873 | 11.218
KING_NW_KINGNW | King Mountain NW | WND | 79 | Wind |  |  | 6.873 | 11.218
KING_SE_KINGSE | King Mountain SE | WND | 40 | Wind |  |  | 3.48 | 5.68
KING_SW_KINGSW | King Mountain SW | WND | 79 | Wind |  |  | 6.873 | 11.218
KUNITZ_WIND_LGE | Kunitz Wind | WND | 40 | Wind |  |  | 3.48 | 5.68
KUNITZ_WIND_NWP | Delaware Mountain Wind Farm | WND | 30 | Wind |  |  | 2.61 | 4.26
LGD_LANGFORD | Langford Wind Power | WND | 155 | Wind |  |  | 13.485 | 22.01
LNCRK_G83 | Mesquite Wind | WND | 200 | Wind |  |  | 17.4 | 28.4
LNCRK2_G871 | Post Oak Wind 1 | WND | 100 | Wind |  |  | 8.7 | 14.2
LNCRK2_G872 | Post Oak Wind 2 | WND | 100 | Wind |  |  | 8.7 | 14.2
LONEWOLF_G1 | Loraine Windpark I | WND | 50 | Wind |  |  | 4.35 | 7.1
LONEWOLF_G2 | Loraine Windpark II | WND | 51 | Wind |  |  | 4.437 | 7.242
LONEWOLF_G3 | Loraine Windpark III | WND | 26 | Wind |  |  | 2.262 | 3.692
LONEWOLF_G4 | Loraine Windpark IV | WND | 24 | Wind |  |  | 2.088 | 3.408
MCDLD_FCW1 | Forest Creek Wind Farm | WND | 124 | Wind |  |  | 10.788 | 17.608
MCDLD_SBW1 | Sand Bluff Wind Farm | WND | 90 | Wind |  |  | 7.83 | 12.78
MOZART_WIND_1 | WKN Mozart | WND | 30 | Wind |  |  | 2.61 | 4.26
MWEC_G1 | McAdoo Wind Farm | WND | 150 | Wind |  |  | 13.05 | 21.3
NWF_NWF1 | Notrees-1 | WND | 153 | Wind |  |  | 13.311 | 21.726
OWF_OWF | Ocotillo Wind Farm | WND | 60 | Wind |  |  | 5.22 | 8.52
PC_NORTH_PANTHER1 | Panther Creek 1 | WND | 143 | Wind |  |  | 12.441 | 20.306
PC_SOUTH_PANTHER2 | Panther Creek 2 | WND | 116 | Wind |  |  | 10.092 | 16.472
PC_SOUTH_PANTHER3 | Panther Creek 3 | WND | 200 | Wind |  |  | 17.4 | 28.4
PYR_PYRON1 | Pyron Wind Farm | WND | 249 | Wind |  |  | 21.663 | 35.358
RDCANYON_RDCNY1 | Red Canyon | WND | 84 | Wind |  |  | 7.308 | 11.928
SENATEWD_UNIT1 | Senate Wind Project | WND | 150 | Wind |  |  | 13.05 | 21.3
SGMTN_SIGNALMT | Texas Big Spring | WND | 34 | Wind |  |  | 2.958 | 4.828
STWF_T1 | South Trent Wind Farm | WND | 101 | Wind |  |  | 8.787 | 14.342
SW_MESA_SW_MESA | West Texas Wind Energy | WND | 74 | Wind |  |  | 6.438 | 10.508
SWEC_G1 | Stanton Wind Energy | WND | 124 | Wind |  |  | 10.788 | 17.608
SWEETWN2_WND2 | Sweetwater Wind 3 | WND | 98 | Wind |  |  | 8.526 | 13.916
SWEETWN2_WND24 | Sweetwater Wind 2 | WND | 16 | Wind |  |  | 1.392 | 2.272
SWEETWN3_WND3A | Sweetwater Wind 4 | WND | 29.5 | Wind |  |  | 2.5665 | 4.189
SWEETWN3_WND3B | Sweetwater Wind 4 | WND | 100.5 | Wind |  |  | 8.7435 | 14.271
SWEETWN4_WND4A | Sweetwater Wind 7 | WND | 118 | Wind |  |  | 10.266 | 16.756
SWEETWN4_WND4B | Sweetwater Wind 6 | WND | 104 | Wind |  |  | 9.048 | 14.768
SWEETWN4_WND5 | Sweetwater Wind 5 | WND | 79 | Wind |  |  | 6.873 | 11.218
SWEETWND_WND1 | Sweetwater Wind 1 | WND | 37 | Wind |  |  | 3.219 | 5.254
TKWSW1_ROSCOE | Roscoe Wind Farm | WND | 209 | Wind |  |  | 18.183 | 29.678
TRENT_TRENT | Trent Wind Farm | WND | 151 | Wind |  |  | 13.137 | 21.442
TRINITY_TH1_BUS1 | Trinity Hills | WND | 118 | Wind |  |  | 10.266 | 16.756
TRINITY_TH1_BUS2 | Trinity Hills | WND | 108 | Wind |  |  | 9.396 | 15.336
TTWEC_G1 | Turkey Track Wind Energy Center | WND | 170 | Wind |  |  | 14.79 | 24.14
WEC_WECG1 | Whirlwind Energy | WND | 57 | Wind |  |  | 4.959 | 8.094
WHTTAIL_WR1 | Wolfe Ridge | WND | 113 | Wind |  |  | 9.831 | 16.046
WOODWRD1_WOODWRD1 | Pecos Wind (Woodward 1) | WND | 83 | Wind |  |  | 7.221 | 11.786
WOODWRD2_WOODWRD2 | Pecos Wind (Woodward 2) | WND | 77 | Wind |  |  | 6.699 | 10.934
COTTON_PAP2 | Papalote Creek Wind | WND | 200 | Wind* |  |  | 17.4 | 65.8
DG_NUECE_6UNITS | Harbor Wind | WND | 9 | Wind* |  |  | 0.783 | 2.961
PAP1_PAP1 | Papalote Creek Wind Farm | WND | 180 | Wind* |  |  | 15.66 | 59.22
PENA_UNIT1 | Penascal Wind | WND | 161 | Wind* |  |  | 14.007 | 52.969
PENA_UNIT2 | Penascal Wind | WND | 142 | Wind* |  |  | 12.354 | 46.718
PENA3_UNIT3 | Penascal Wind | WND | 101 | Wind* |  |  | 8.787 | 33.229
REDFISH_MV1A | Magic Valley Wind | WND | 103 | Wind* |  |  | 8.961 | 33.887
REDFISH_MV1B | Magic Valley Wind | WND | 103 | Wind* |  |  | 8.961 | 33.887
TGW_T1 | Gulf Wind I | WND | 142 | Wind* |  |  | 12.354 | 46.718
TGW_T2 | Gulf Wind II | WND | 142 | Wind* |  |  | 12.354 | 46.718
| Total Wind Resources |  | 10406.5 |  |  |  | 905.3655 | 1717.644
BLSUMMIT_BLSMT1_5 | Blue Summit Windfarm 1 | WND | 9 | New |  |  | 0.783 | 1.278
BLSUMMIT_BLSMT1_6 | Blue Summit Windfarm 2 | WND | 126.4 | New |  |  | 10.9968 | 17.9488
BCATWIND_WIND_1 | Bobcat Bluff | WND | 150 | New |  |  | 13.05 | 21.3
LV1_LV1B | Los Vientos 1 | WND | 201.6 | New* |  |  | 17.5392 | 66.3264
LV1_LV1A | Los Vientos 2 | WND | 200.1 | New* |  |  | 17.4087 | 65.8329
| Total Planned Wind Resources |  | 687.1 |  |  |  | 59.7777 | 172.6861
| Net Impact of Proposed ELCC |  | 925.1869
APD_APD_G1 | APPLIED ENERGY | PC | 140 | Currently Unavailable (Mothballed)
ATKINS_ATKINSG3 | ATKINS | NG | 12 | Currently Unavailable (Mothballed)
ATKINS_ATKINSG4 | ATKINS | NG | 22 | Currently Unavailable (Mothballed)
ATKINS_ATKINSG5 | ATKINS | NG | 25 | Currently Unavailable (Mothballed)
ATKINS_ATKINSG6 | ATKINS | NG | 50 | Currently Unavailable (Mothballed)
GBY_GBYGT82 | GREENS BAYOU | NG | 58 | Currently Unavailable (Mothballed)
LEON_CRK_LCP3G3 | LEON CREEK | NG | 60 | To be retired 4/1/2013
LEON_CRK_LCP4G4 | LEON CREEK | NG | 95 | To be retired 4/1/2013
MNSES_UNIT1 | MONTICELLO SES | SUB | 580 | Currently Unavailable (Mothballed)
MNSES_UNIT2 | MONTICELLO SES | SUB | 580 | Currently Unavailable (Mothballed)
NTX_NTX_1 | NORTH TEXAS | NG | 18 | Currently Unavailable (Mothballed)
NTX_NTX_2 | NORTH TEXAS | NG | 18 | Currently Unavailable (Mothballed)
NTX_NTX_3 | NORTH TEXAS | NG | 39 | Currently Unavailable (Mothballed)
PBSES_UNIT6 | PERMIAN BASIN SES | NG | 520 | Currently Unavailable (Mothballed)
SILASRAY_SILAS_5 | SILAS RAY | NG | 10 | Currently Unavailable (Mothballed)
SRB_SRB_G1 | SR BERTRON | NG | 118 | Currently Unavailable (Mothballed)
SRB_SRB_G2 | SR BERTRON | NG | 174 | Currently Unavailable (Mothballed)
SRB_SRBGT_2 | SR BERTRON | NG | 13 | Currently Unavailable (Mothballed)
SRB_SRB_G3 | SR BERTRON | NG | 230 | Currently Unavailable (Mothballed)
SRB_SRB_G4 | SR BERTRON | NG | 230 | Currently Unavailable (Mothballed)
VLSES_UNIT1 | VALLEY SES | NG | 174 | Currently Unavailable (Mothballed)
VLSES_UNIT2 | VALLEY SES | NG | 520 | Currently Unavailable (Mothballed)
VLSES_UNIT3 | VALLEY SES | NG | 375 | Currently Unavailable (Mothballed)
WND_WHITNEY1 | WHITNEY DAM | WAT | 15 | Currently Unavailable (Mothballed)
| Total Unavailable (Mothballed) Resources |  | 4076
* Coastal Wind
Note: Capacity Information Current as of 2/15/2013

## Background
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. Several sensitivity analyses are developed by varying the values of certain parameters that affect resource adequacy. The variation in these parameters are based on historic values , adjusted by any known or expected change.