ERCOT Operations Report

August 2013 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 8/2/2013 15:35 | 59.830 | 143 | Unit trip with approximately 916 MW net |
| 8/11/2013 5:43 | 59.839 | 22 | Unit trip with approximately 826 MW net |
| 8/12/2013 2:58 | 59.818 | 41 | Unit trip with approximately 818 MW net. |
| 8/16/2013 16:34 | 59.898 | 1 | Unit trip with approximately 304 MW net. |
| 8/18/2013 16:45 | 59.865 | 63 | Unit trip with approximately 605 MW net. |
| 8/20/2013 14:16 | 59.894 | 5 | DC Tie trip with approximately 599 MW net |
| 8/24/2013 6:46 | 59.846 | 70 | Unit trip with approximately 576 MW net |
| 8/29/2013 18:55 | 59.878 | 14 | Unit trip with approximately 805 MW net |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

ERCOT evaluates PMU data according to industry standards.  Industry standards specify that damping 	ratio for larger oscillations should be 3.0% or greater.  All events listed below indicate the ERCOT 	system 	transitioned well after each disturbance.

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 8/2/2013 15:34:53 | Unit Trip | Approx. 307 sec | The event was caused by the loss of one unit. The unit was generating 918 MW net before the trip, the frequency dropped to 59.827 Hz. The two oscillating frequencies of 0.48 Hz with 7.58% damping ratio and 0.72 Hz with 6.8% damping ratio were observed. |
| 8/11/2013 05:43:25 | Unit Trip | Approx. 194 sec | The event was caused by the loss of one unit. The unit was generating 826 MW net before the trip, the frequency dropped to 59.836 Hz. The oscillating frequency of 0.34 Hz with 19.7% damping ratio was observed. |
| 8/12/2013 02:58:01 | Unit Trip | Approx. 285 sec | The event was caused by the loss of one unit. The unit was generating 793 MW net before the trip, the frequency dropped to 59.815 Hz. The oscillating frequency of 0.64 Hz with 5.98% damping ratio was observed. |
| 8/18/2013 16:45:31 | Unit Trip | Approx. 147 sec | The event was caused by the loss of one unit. The unit was generating 606 MW net before the trip, the frequency dropped to 59.865 Hz. The oscillating frequency of 0.9 Hz with 15.0% damping ratio was observed. |
| 8/20/2013 14:19:06 | Unit Trip | Approx. 120 sec | The event was caused by the loss of one unit. The unit was generating 600 MW net before the trip, the frequency dropped to 59.893 Hz. The oscillating frequency of 0.59 Hz with 8.4% damping ratio was observed. |
| 8/24/2013 18:46:06 | Unit Trip | Approx. 173 sec | The event was caused by the loss of one unit. The unit was generating 576 MW net before the trip, the frequency dropped to 59.846 Hz. The oscillating frequency of 1.0 Hz with 3.19% damping ratio was observed. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 8/2/13 15:35:14 | 8/2/13 15:40:57 | 0:05:43 | 656.2 |  |
| 8/11/13 5:43:42 | 8/11/13 5:47:54 | 0:04:12 | 367 |  |
| 8/12/13 2:58:10 | 8/12/13 3:04:06 | 0:05:56 | 748.9 |  |
| 8/16/13 16:34:22 | 8/16/13 16:37:14 | 0:02:52 | 21.1 |  |
| 8/18/13 16:45:38 | 8/18/13 16:48:54 | 0:03:16 | 244.7 |  |
| 8/20/13 14:19:18 | 8/20/13 14:21:54 | 0:02:36 | 42.3 |  |
| 8/24/13 18:46:14 | 8/24/13 18:49:38 | 0:03:24 | 453.5 |  |
| 8/29/13 18:55:28 | 8/29/13 18:59:20 | 0:03:52 | 554.0 |  |

RUC Commitments

No units committed through RUC process.

SCED Congestion Management Activity

Congestion affected by outages

| Contingency Description | Overloaded Element | Total |
| --- | --- | --- |
| Midland East - Moss Switch 345kV | Odessa - Odessa North 138kV | 31 |
| Morgan Creek Ses Axfmr2h (3) 345/138 kV | Morgan Creek Ses Axfmr1l 345/138kV | 21 |
| Cagnon Axfmr3l-H (3)345/138kV | Cagnon AXFMR4H 345/138kV | 13 |
| Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 11 |
| Morgan Creek - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 9 |
| Laquinta - Lobo 138 kV | Falfur 138_69A1 138/69kV | 9 |
| Calallen Sub to Lon_hill 69kV | Lon Hill - Robstown Tap 69 kV | 8 |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 7 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Laquinta - Lobo 138 kV | 6 |
| DCKT Marion - Zorn and Clear Springs 345 KV | Seguin - Seguin West 138 kV | 6 |
| China Grove Switch - Morgan Creek Ses 138 kV (6220) | China Grove Switch - Morgan Creek Ses 138 KV (6225) | 5 |
| DCKT Jewett - Singleton 345kV | Twin Oak Switch - Btu_Jack_Creek 345 KV | 5 |
| Golden Switch - Sun Switch 138 kV | Ennis Creek Switch Axfmr1 138/69 kV | 4 |
| Euless - Dfw D-West - Dfw Southwest - Dfw E-East - Ligget Switch 138 kV | Dfw D-East 1 - Dfw C-East 138kV | 4 |
| Fort Stockton Plant - Barrilla 138kV | Fort Stockton Switch - Barrilla 69 kV | 3 |
| Big Wells - Dilley Switch Aep 138kV | West Batesville - Asherton 138kV | 3 |
| DCKT Euless - Ligget Switch 138 kV | Dfw D-East 1 - Dfw C-East 138kV | 3 |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Sinton - Skidmore 69 kV | 3 |
| DCKT Marion - Hill Country and Skyline 345 kV | Marion - Cibolo 138 kV | 3 |
| Snyder - Sacroc 138 kV | Ennis Creek Switch Axfmr1 138/69 kV | 2 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | San Diego - Freer 69 kV | 2 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | North Laredo Switch - Mines Rd 138 kV | 2 |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 2 |
| Medow - Ph Robinson 345 kV | Hastings Tnp - Friendswood 138 kV | 2 |
| DCKT Salado Switch - Killeen Switch 345kV (271 & 272) | Belton - Belton Southwest 138 kV | 2 |
| DCKT Olinger - Firewheel and Elmgrove 138 kV | Olinger - Ben Davis 138 kV | 2 |
| China Grove Switch - Morgan Creek Ses 138 kV (6225) | China Grove Switch - Morgan Creek Ses 138 kV (6220) | 2 |
| Cheyenne - Cheyenne Tap 138kV | Holt Switch - Amoco Midland Farms Tap 138 kV | 2 |
| Mesa View Switch - Fort Lancaster 138 kV | Big Lake - Big Lake Phillips Tap 69kV | 2 |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345 kV (260_A) | 2 |
| Ph Robinson At3_H (3)345/138kV | Ph Robinson At1 (3) 345/138kV | 2 |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Rincon - Bonnieview 69kV | 2 |
| Utopia - Bandera Lcra 69 kV | Uvalde Aep 138_69A1 468/69kV | 2 |
| Whitestone - Buttercup 138 kV | Marchall Ford - Lago Vista 138 kV | 2 |
| Midland East - Moss Switch 345kV | Odessa EHV Switch- Big Three Odessa Tap 138kV | 1 |
| Falcon Seaboard - Midland East 345 kV | Stanton East - 1276 Triangle 138kV | 1 |
| Airline Aep - Cabaniss - Westside Aep 138 kV | Barney Davis - Rodd Field 138 kV | 1 |
| Pawnee Switching Station - Lon Hill 345 kV | Sinton - Skidmore 69 kV | 1 |
| DCKT Trinidad Ses - Watermill Switch & Tri Corner 345kV | Forest Grove Switch - Mabank Tap 138kV | 1 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Pearsall Switching Station - Paloduro Sub 138 kV | 1 |
| Lobo 2_345_138_H 345/138 KV | Laquinta - Lobo 138 kV | 1 |
| DCKT Comanche Peak Units 1 and 2 | Victoria - Magruder 138 kV (Magrud_Victor2) | 1 |
| DCKT South Texas Project Units 1 and 2 | Lolita - Blessing 138kV | 1 |
| DCKT Austrop - Garfield and Zorn 345 kV | Garfield AT1 345/138 kV | 1 |
| Medow - Ph Robinson 345 kV | Alvin Tnp - Freeway Park Tnp 138kV | 1 |
| Bosque Switch - Elm Mott 345kV | Bosque Switch - Rogers Hill Bepc 138kV | 1 |
| DCKT Carrollton - Hackberry - Norwood Switch 345 kV | Dfw D-East 1 - Dfw C-East 138kV | 1 |
| Hiway 9 - Citgo N Oak Park 138 kV | Nueces Bay - Morris Street 138kV | 1 |
| DCKT Monticello Ses - Allen Switch - Royse Switch 345 kV | Apollo - Richardson east 138 kV | 1 |
| DCKT Martin Lake Ses - Elkton and Tyler Grande 345 kV and Stryker Creek Ses Unit 2 | Tyler Northwest - Tyler West 138 kV | 1 |
| DCKT Martin Lake Ses - Elkton and Tyler Grande 345 kV and Stryker Creek Ses Unit 2 | Shamburger Switch - Tyler Northwest 138 kV | 1 |
| Everman Switch Axfrm3 (3) 345/138 kV | Everman Switch Axfmr2 (3) 345/138 kV | 1 |
| Escondido - Asherton 138 kV | Bracketville - Hamilton Road 138 kV | 1 |
| Bracketville - Odlaw Switchyard & Hamilton Road 138kV | Uvalde Aep 138_69A1 468/69kV | 1 |
| Cedar Hill Switch Axfmr2l (3) 345/138kV | Sherry Switch - Park Row 138 kV (6325) | 1 |
| Illinois #4 - Fort Lancaster 138kV | Friend Ranch - Ozona 69kV | 1 |
| DCKT Skyline - Calaveras 345kV | Cagnon AXFMR3 345/138 kV | 1 |
| Cagnon Axfmr3l-H (3)345/138kV | Cagnon AXFMR4H 345/138kV | 1 |
| Eskota Switch Axfmr1 138/69kV | Abilene Northwest - Ely Rea Tap 69kV | 1 |
| Morgan Creek Ses Axfmr2h (3) 345/138 kV | Morgan Creek Ses Axfmr1h 345/138kV | 1 |
| DCKT Lytton Springs - Slauger Lane & Turnersville 138kV | Lytton Springs - Pilot Knob 138kV | 1 |
| Btu_Atkins - Btu_Dansby 138kV | Btu_Nall_Lane - Btu_Braiacrest 69kV | 1 |
| Friend Ranch - Fort Lancast 138kV | Ozona - Friend Ranch 69 kV | 1 |
| DCKT Jefferson - Pasedena 138 kV and Deepwater - South Houston 69 kV | Conial - Waburn 138 kV | 1 |
| Anna Switch - Collin Switch 345 kV 345 kV | Payne Switch - Epco Poi 138 kV | 1 |
| DCKT Th Wharton - Camron and Satsuma 138 kV | Th Wharton AT1T 345/138 kV | 1 |
| Dilley2 - Dilley Switch Aep 69 kV | Pearsall - Moores 69 kV | 1 |
| Mabank Tap - Malakof 138 kV | Athens - Trinidad Ses 69 kV | 1 |
| Norwood Switch Axfmr1h 345/138 kV | Amelia Street - Ut Southwest Medical Center 138 kV (3415) | 1 |
| Cssc - Csswcs 138 kV | Gibbons Creek - Btu_Greens_Prairie 138 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 0 |

Congestion Cost

Binding Constraints – Year to Date

| Contingency | Binding Element | Number of 5-min intervals | Shadow Price Range $/MWh | Estimated Congestion Rent $ (Shadow Price*Limit) | Transmission Project |
| --- | --- | --- | --- | --- | --- |
| Midland East to Odessa EHV 345 kV & Moss Switch 345/138 kV Xfmr | Odessa - Odessa North 138 kV | 7111 | 0 - 3500 | 50,380,818 | 13TPIT0136, 14TPIT0054 |
| Roanoke Switch - West Denton 345 kV & Roanoke Switch - Lewisville Switch 345 kV; or West Denton - Roanoke Switch 345 kV; or West Denton - Rdwells 138 kV | Jim Cristal - North Denton 138kV | 1407 | 0 - 3500 | 18,679,874 | 14TPIT0047 |
| Sun Switch - Golden Switch 138 kV; Sun Switch - Morgan Creek SES 138 kV | Bluff Creek Switch - China Grove Switch 138 kV | 1037 | 0 - 3500 | 17,678,573 | 12TPIT0058, 13TPIT0098 |
| Roanoke Switch - West Denton 345 kV & Roanoke Switch - Lewisville Switch 345 kV; or West Denton - Roanoke Switch 345 kV | Fort Worth - Teasley 138 kV | 2813 | 0 - 3500 | 16,898,845 | 14TPIT0047 |
| Amoco South Foster to Westover 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1204 | 0 - 3500 | 15,801,329 | 13TPIT0098, 13TPIT0093 |
| Austrop 345/138 kV Xfmr & Garfield LCRA 345/138 kV Xfmr | Austrop 345/138 kV Xfmr | 1965 | 0 - 4500 | 11,898,409 | 10TPIT0031 |
| Morgan Creek SES 345/138 kV Autotransformer 2 | Morgan Creek SES 345/138 kV Autotransformer 4 | 131 | 29 - 4500 | 11,206,208 |  |
| West Denton - Rdwells 138 kV | Teasley - Pockrus Substation 138 kV | 939 | 0 - 3500 | 11,088,886 | 5YTP [2012-R46] |
| Morgan Creek SES AXFMR2 345/138kV | Mogan Creek SES AXFMR1 345/138kV | 3215 | 0 - 489 | 8,954,483 |  |
| Ajo - Rio Hondo 345 kV | North Edinburg - Lon Hill 345 kV | 39 | 2 - 4500 | 7,633,932 | 14TPIT0050 |
| McNeil - Gilleand Creek 138 kV | Hutto - Round Rock NE 138 Kv | 1644 | 0 - 3500 | 7,305,704 |  |
| DCKT Roansprairie - Kuykendahl - King & Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 2007 | 0 - 4500 | 7,026,709 |  |
| Garfield LCRA 345/138 kV Xfmr & Austrop - Daffin 138 kV | Austrop - Dunlap 138 kV | 740 | 0 - 3500 | 6,752,182 | 10TPIT0031 |
| Odlaw Switchyard to Uvalde AEP 138kV | Hamilton Road - Maverick 138kV | 5676 | 0 - 2905 | 6,457,873 | 16TPIT0024 |
| Wink 138/69 kV Autotransformer; or Wink - Wink Sub 138 kV | Wink Basin Tap - Wink Sub 69 kV | 772 | 0 - 2800 | 6,378,270 | 13TPIT0220 |
| Calallen Sub to Lon Hill 69kV | Lon Hill - Robstown Tap 69kV | 559 | 0 - 2800 | 6,139,843 | 12TPIT0181 |
| Meadow - PH Robinson 345 kV | Alvin - Freeway Park 138 kV | 2566 | 0 - 3500 | 4,946,205 |  |
| China Grove Switch to Morgan Creek SES 138kV | China Grove Switch - Morgan Creek SES 138kV | 115 | 0 - 3500 | 4,399,879 | 12TPIT0058, 13TPIT0098 |
| Garfield - Hicross & Garfield - Onion Creek 138 kV | Austrop - Daffin 138 kV | 1033 | 0 - 3500 | 4,052,209 | 10TPIT0031 |
| Cagnon AXFMR3 345/138kV | Cagnon AXFMR4 345/138kV | 1571 | 0 - 4500 | 3,984,496 | 14TPIT0031 |

Binding Constraints – August 2013

| Contingency | Binding Element | Number of 5-min intervals | Shadow Price Range $/MWh | Estimated Congestion Rent $ (Shadow Price*Limit) | Transmission Project | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Midland East to Odessa EHV 345 kV & Moss Switch 345/138 kV Xfmr | Odessa - Odessa North 138 kV | 2720 | 5 - 3500 | 21,390,660 | 13TPIT0136, 14TPIT0054 | High load and low wind conditions |
| Sun Switch to Morgan Creek Switch 138kV; Sun Switch to Morgan Creek Switch 138kV; Sun Switch - Golden Switch 138 kV | Bluff Creek Switch - China Grove Switch 138kV | 228 | 21 - 3500 | 4,397,866 | 12TPIT0058, 13TPIT0098 | High load and low wind conditions |
| Calallen Sub to Lon Hill 69kV | Lon Hill - Robstown Tap 69kV | 338 | 0 - 2800 | 3,901,446 | 12TPIT0181 | High load |
| Morgan Creek SES AXFMR2 345/138kV | Mogan Creek SES AXFMR1 345/138kV | 1037 | 0 - 489 | 3,316,093 |  | High load and low wind conditions |
| China Grove Switch to Morgan Creek SES 138kV | China Grove Switch - Morgan Creek SES 138kV | 67 | 9 - 3500 | 2,908,162 | 12TPIT0058, 13TPIT0098 | High load and low wind conditions |
| Everman Switch AXFMR3 345/138kV | Everman Switch AXFMR2 345/138kV | 8 | 2264 - 4500 | 959,858 |  | Local outage |
| Orange Grove Switching Station to Lon Hill 138kV | Lon Hill - Smith 69kV | 411 | 3 - 2038 | 835,429 | 16TPIT0026 | High load |
| Big Wells to Dilley Switch AEP 138kV | Asherton - West Batesville 138kV | 51 | 4 - 3500 | 779,921 |  | High load |
| DCKT Roansprairie - Kuykendahl - King & Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 146 | 0 - 2745 | 699,042 |  | High load |
| China Grove Switch to Morgan Creek SES 138kV | China Grove Switch - Morgan Creek SES 138kV | 17 | 20 - 3500 | 579,745 | 12TPIT0058, 13TPIT0098 | High load and low wind conditions |
| Norwood Switch AXFMR1 345/138kV | Amelia Street - UT Southwest Medical Center 138kV | 10 | 3500 - 3500 | 569,246 | 11TPIT0097 | Local outage |
| Whitestone to Buttercup 138kV | Lago Vista - Mashall Ford 138kV | 11 | 105 - 3500 | 499,041 | 15TPIT0061 | Local outage |
| DCKT Singleton to Jewet 345kV | Twin Oak Switch - BTU_Jack_Creek 345kV | 295 | 0 - 453 | 477,401 |  | High load |
| Ph Robinson AT3 345/138kV | Ph Robinson AT1 345/138kV | 11 | 8 - 3500 | 392,578 |  | Local outage |
| Cssc to Csswcs 138kV | Gibbons Creek - BTU_Green_Prarie 138kV | 6 | 3500 - 3500 | 381,208 |  | Local outage |
| DCKT Th Wharton to Camron and Satsuma 138kV | Th Wharton - Th Wharton 138kV | 8 | 66 - 3500 | 349,563 |  | High local generation and Houston load |
| DCKT Salado Swith to Killeen Switch 345kV | Belton - Belton Southwest 138kV | 38 | 11 - 1005 | 348,479 | 17TPIT0028 | High load and low wind condition |
| Liggett Switch to DFW D-West 138kV | DFW D-East 1 - DFW C-East 138kV | 27 | 1 - 3500 | 346,677 | 07TPIT0001 07TPIT0002 | High load |
| Cagnon AXFMR3 345/138kV | Cagnon AXFMR4 345/138kV | 237 | 0 - 107 | 343,594 | 14TPIT0031 | High load |
| Lobo to San Miguel 345/138kV | Laqunita - Lobo 138kV | 157 | 0 - 138 | 297,182 | 16TPIT0020 15TPIT0052 | High Valley load and low wind |

Wind Generation as a Percent of Load

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

Permian Basin SPS was approved

China Grove SPS was temporarily disabled

New Procedures/Forms/Operations Bulletins

| Power Operations Bulletin 637 - Real Time Desk V1 Rev25 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Power Operations Bulletin 638 - Reliability Unit Commitment Desk V1 Rev21 |  |  |  |  |  |
| Power Operations Bulletin 639 - Resource Desk V1 Rev24 |  |  |  |  |  |
| Power Operations Bulletin 640 - Shift Supervisor Desk V1 Rev22 |  |  |  |  |  |
| Power Operations Bulletin 641 - Transmission and Security Desk V1 Rev25 Power Operations Bulletin 642 - Shift Supervisor Desk V1 Rev23 Power Operations Bulletin 643 - Transmission and Security Desk V1 Rev26 Power Operations Bulletin 644 – DC Tie Desk V1 Rev22 |  |  |  |  |  |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

08/16 03:10	ERCOT issued Emergency Notice due to SCED (Security Constrained Economic Dispatch) execution failure.

Communication Issues

None

## ERCOT peak (Unofficial)

08/07 17:00 67,180 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 | 2.83 |
| March | 2.24 | 2.02 | 3.49 | 2.68 |
| April | 2.47 | 3.55 | 2.78 | 2.81 |
| May | 2.63 | 3.27 | 3.09 | 3.12 |
| June | 2.84 | 2.28 | 2.85 | 2.51 |
| July | 2.39 | 1.63 | 2.85 | 2.70 |
| August | 2.29 | 2.28 | 2.96 | 2.07 |
| September | 3.14 | 2.70 | 3.43 |  |
| October | 2.37 | 3.51 | 2.99 |  |
| November | 3.46 | 3.38 | 2.90 |  |
| December | 2.60 | 2.99 | 3.47 |  |
| Annual Average | 2.83 | 2.83 | 3.02 | 2.91 |

OCN, Advisory, Watch & Emergency Notices

Capacity

OCN

None

Advisory

| Date | Event |
| --- | --- |
| 8/5/2013 08:35 | ERCOT issued Advisory due to extreme hot weather expected in the North Central and South Central weather zones for August 7th. |
| 8/6/2013 08:35 | ERCOT issued Advisory due to extreme hot weather expected in the North Central and South Central weather zones for August 8th |

Transmission Watch

None

Watch

None

Emergency Notice

8/16 03:10	ERCOT issued an emergency notice due to SCED execution failure.

Texas RE Event Analysis

None

Additional Information

8/7/2013	Approximately 82 MW of load was dropped in Southeast Texas because an outage was taken in error. The ERCOT Study Network Analysis Application tool has a bug that provided false information to the Outage Coordinator.  Due to the software glitch, an outage was approved and taken on a radial feed.  There were proper communications between the affected TOPs; however they failed to expose the problem.  ERCOT has initiated a Change Request to correct the problem, and implemented additional measures to prevent reoccurrence until the glitch is fixed.