## Slide 1
NPRR425 - Creation of a WGR Group for GREDP and Base Point Deviation Evaluation and Mixing Turbine Types Within a WGR
Art Deller, P.E.
ROS 9/12/13

## Slide 2: Agenda
Changes specified in the NPRR
Changes required of the RARF
Next Steps

## Slide 3: Business Case for NPRR425
Qualitative benefits:
Maintains current WGR definition for reactive modeling purposes while addressing Dispatch issues for Resource Entities representing WGRs.
Accuracy and transparency of Base Point Deviation and GREDP calculations for WGRs that can only be controlled as a WGR Group.

## Slide 4: WGR Aggregation
“A Resource Entity may aggregate wind turbines together to form a WGR if the turbines are connected to the same Electrical Bus at the POI and are the same model and size, and the aggregation does not reduce ERCOT’s ability to model pre- and post-contingency conditions.”
If:
  The mix of wind turbine models and sizes causes no degradation in the dynamic performance
  The mix of wind turbines are included in the Resource asset registration information submitted for the WGR;
  All relevant wind turbine data requested by ERCOT is provided
  With the addition of dissimilar wind turbines, the existing WGR shall continue to meet the applicable Protocol performance requirements
  Either
    No more than the lower of 5% or ten MW aggregate capacity is of wind turbines that are not the same model or size from the turbines within the existing WGR; or
    The wind turbines that are not the same model or size meet the following criteria:
      (A) The wind turbines have similar dynamic characteristics to the existing WGR, as determined by ERCOT in its sole discretion;
      (B) The MW capability difference of each wind turbine is no more than10% of each wind turbine’s maximum MW rating; and
      (C) The manufacturer’s power curves for the wind turbines have a correlation of 0.95 or greater with the other wind turbines within the existing WGR over wind speeds of 0 to 18 m/s.

## Slide 5: WGR Grouping
Wind-powered Generation Resource (WGR) Group
A group of two or more WGRs whose performance in responding to SCED Dispatch Instructions will be assessed as an aggregate for Generation Resource Energy Deployment Performance (GREDP) and Base Point Deviation. A WGR Group cannot contain any WGRs that are Split Generation Resources. Additionally, only WGRs that have the same Resource Node can be mapped to a WGR Group. Resource Entities can choose to group WGRs and shall provide the grouping information in a timely manner for ERCOT review prior to the scheduled database loads.

## Slide 6: RARF Changes
Grouping
Add values on the Turbine Details Tab (renamed from Unit Info – Turbine)
  WGR Group
  Group Code (Internal Only)
  Site Group (Internal Only)
  Turbine Manufacturer/Model (moved from Planning Wind, renamed)
  Turbine Type (1, 2, 3, 4, 5)

## Slide 7: RARF Changes
Aggregation
Moved data to support Wind Aggregation
  Added Planning values to Turbine Details tab (data to be provided per turbine)
  Possibly removing Planning data from the Planning-Wind tab
Other
  Controlled Fault Current Magnitude for Types 3 & 4

## Slide 8: RARF Changes (Cont.)
Removed from PLANNING - WIND | Added to TURBINE DETAILS
WIND GENERATION GROUP DETAILS | 
Resoure Name (Unit Code/Mnemonic) | Resoure Name (Unit Code/Mnemonic)
 | WGR Group
 | Group Code (Hidden field on Form)
 | Site Group
TURBINE DETAILS | 
Type of Turbine (Manufacturer/Model) | Turbine Manufacturer/Model
MW Rating for this model of Turbine | MW Rating for this model of Turbine
Number of this type of Turbine | Number of Turbine Manufacturer/Model
 | Turbine Type (1,2,3,4,5)
PLANNING DETAILS | 
What is the Mva Base That the Following Data Is Based On? | What is the Mva Base That the Following Data Is Based On?
What Is The Kv Base That The Following Data Is Based On? | What Is The Kv Base That The Following Data Is Based On?
Direct Axis Subtransient Reactance, X"di (unsaturated) | Subtransient Reactance X'',(Instantaneous Fault Current Period) (unsaturated)
Direct Axis Transient Reactance, X'di (unsaturated) | Transient Reactance, X' (First 2-3 cycles of the Fault) (unsaturated)
Positive Sequence Z (unsaturated) - R | Positive Sequence Resistance (unsaturated)
Positive Sequence Z (unsaturated) - R | Synchronous Reactance X (After 4 cycles of the fault) (unsaturated)
Negative Sequence Z (unsaturated) - R | Negative Sequence Z (unsaturated) - R
Negative Sequence Z (unsaturated) - R | Negative Sequence Z (unsaturated) - X
Zero Sequence Z (unsaturated) - R | Zero Sequence Z (unsaturated) - R
Zero Sequence Z (unsaturated) - R | Zero Sequence Z (unsaturated) - R

## Slide 9: RARF Changes (Cont.)
Removed from PLANNING - WIND | Added to TURBINE DETAILS
PLANNING DETAILS | 
Direct Axis Subtransient Reactance, X"dv (saturated) | Subtransient Reactance X'',(Instantaneous Fault Current Period) (saturated)
Direct Axis Transient Reactance, X'dv (saturated) | Transient Reactance, X' (First 2-3 cycles of the Fault) (saturated)
Positive Sequence Z (saturated) - R | Positive Sequence Resistance (saturated)
Positive Sequence Z (saturated) - X | Synchronous Reactance X (After 4 cycles of the fault) (saturated)
Negative Sequence Z (saturated) - R | Negative Sequence Z (saturated) - R
Negative Sequence Z (saturated) - X | Negative Sequence Z (saturated) - X
Zero Sequence Z (saturated) - R | Zero Sequence Z (saturated) - R
Zero Sequence Z (saturated) - X | Zero Sequence Z (saturated) - X
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Grounding Resistance For An Impedance Grounded Generator In P.U. (100 Mva Base)
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Grounding Reactance For An Impedance Grounded Generator In P.U. (100 Mva Base)
 | Instantaneous Controlled Fault Current Magnitude (% of full load current) for Turbine Types 3 & 4
 | Controlled Fault Current Magnitude At 2 to 3 cycles after fault (% of full load current) for Turbine Types 3 & 4
 | Controlled Fault Current Magnitude At 4 plus cycles after fault (% of full load current) for Turbine Types 3 & 4

## Slide 10: RARF Changes (Cont.)
Removed from PLANNING - WIND | Added to TURBINE DETAILS
TURBINE STEP-UP TRANSFORMER DATA | 
High Side Voltage Level (nominal) | High Side Voltage Level (nominal)
Low Side Voltage Level (nominal) | Low Side Voltage Level (nominal)
High Side Voltage Connection | High Side Voltage Connection
Low Side Voltage Connection | Low Side Voltage Connection
Impedance Z | Impedance Z
X/R Ratio | X/R Ratio
Zero Sequence Z | Zero Sequence Z
Zero Sequence X/R Ratio | Zero Sequence X/R Ratio
Base Mva For Transformer Data | Base Mva For Transformer Data

## Slide 11: Next Steps
Finalize validation rules
Update Glossary and Guide
Release in December 2013
Generate new WGR RARFs
WGRs to re-Submit updated RARFs

## Slide 12
?