## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: August Meeting
Met August 26, 2013
  20 members representing 13 companies as well as ERCOT & TRE.
NPRR 486/ SCR 773 – update
FRRS – discussion
Event review
Frequency Control Report August 2013

## Slide 3: NPRR 486/ SCR 773 update
Reviewed SCR773 in an open forum with WebEx
Q1: Does SCR 773 address the problem identified in NPRR 486?
A1: There is improvement, but the problem has not yet been solved.
Q2: What is market objective of NPRR 486?
A2: To minimize the unpriced energy between SCED runs.
Q3: What is the reliability objective of NPRR 486?
A3: To minimize the regulation deployment bias and to maintain the appropriate amount of operating reserves held in reserve. Decrease Regulation exhaustion rate(normalized across different years).
Q4: Has the reliability objective been met?
A4: Partial improvement has been shown.
Q5: What are next steps for reliability concerns?
A5: Evaluate metrics/targets for reporting to ROS. More root cause analysis during chronic regulation bias intervals.

## Slide 4: NPRR 486/ SCR 773 cont
Evaluation and changes going forward
  Purely Integrated feedback was discussed
  Suggested that ERCOT evaluate using a PID type controller scheme
  Data will be gathered for review at September meeting
    Generation deviation
    Regulation bias
    PID scheme & modeled results if possible
    Regulation zero crossings
More work to be done…

## Slide 5: NPRR 486/SCR773
Requests of ROS:
  Provide feedback on the analysis to date
  Provide direction on evaluation objectives going forward

## Slide 6: FRRS data and deployment review
Recommend proportional response/deployment
ERCOT presented 3 options
  Adjust the granularity for deployment to 6 steps
  Adjust the granularity for deployment to 3 steps
  Redesign the deployment to a straight line function that matches approximately 0.04% droop

## Slide 7: FRRS Cont.
Option 1: Adjust the granularity for deployment to 6 steps
  Parameter changes are needed to add the extra granularity
  Mid term solution
Option 2: Adjust the granularity for deployment to 3 steps
  Parameter changes are needed to add the extra granularity
  Near term solution
  PDCWG recommended option
Option 3:Redesign the deployment to a straight line function that matches approximately 0.04% droop
  Code changes are needed
  Long term solution
  Recall function will need to be designed
ERCOT has action to prepare data for deep dive in September meeting.

## Slide 8: Event Review
PDCWG Reviewed 6 events
  Event resulted in good system frequency performance with few poor performers identified
  Non Frequency responsive RRS providers were noted and ERCOT will follow up with QSEs regarding their performance

## Slide 9: ERCOT Frequency Control Report
Sydney Niemeyer NRG Energy
September 4, 2013

## Slide 10: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.
ERCOT total Time Error Correction time is from NRG data.

## Slide 19
60.010 <= HZ < 60.015

## Slide 23
Time Correction History

## Slide 26
ERCOT Primary Frequency Response – BAL-003-1
2014 Bias and Frequency Response Measure

## Slide 30: Focus for 2013
Formal & documented review/report of frequency responsiveness for Power Augmentation on Combined Cycle Resources (train not individual unit)
Review regulation/GTBD deployment effectiveness (SCR 773)
Pilot of fast frequency response – characterize & create evaluation process.
Ancillary Service Overhaul (new)
No performance required for nonpayment (freq. resp AS)
Study the impact of HSL/basepoint/generation deviation on compliance and reliability
Responsive Reserve requirements, qualification vs. compliance. (10min vs. 16 second)
Standardized/consistent metrics for PFR analysis (BAL001-TRE).
Standardized/reasonable expectations for extreme events (2750MW or larger lost) – driven by NERC.
ERS impact review with appropriate ERCOT group. Target Q1-2014
PMU data understanding of implications
Work on realistic measurement of combined cycles
Red = Work on going
Check = completed goal

## Slide 31
Questions?