| NOGRR Number | 109 | NOGRR Title | Revisions to Definition of Credible Single Contingency for Operations Planning |
| --- | --- | --- | --- |

| Date | June 14, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Ebby John |
| E-mail Address | ebby.john@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2136 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

Comments

CenterPoint Energy appreciates the opportunity to provide comments on this topic.  The Company suggests that the term Credible Single Contingency for Operations Planning be shortened to simply Credible Single Contingency.  This will better align with the language in Nodal Operating Guide Revision Request (NOGRR) 114, Synchronization with NPRR540, Clarification of Credible Single Contingency, as well as Nodal Protocol Revision Request (NPRR) 540, Clarification of Credible Single Contingency.

Revised Proposed Guide Language

1.4	Definitions

Credible Single Contingency

(1)	A single facility, comprised of transmission line, auto transformer, or other associated pieces of equipment.  This includes multiple equipment Outaged or interrupted during a single fault (single fault multiple element (SFME)).

(2)	The Forced Outage of a double-circuit transmission line (DCKT) in excess of 0.5 miles in length will always be considered a credible single contingency for all security constrained unit commitment and energy deployment decisions.

(3)	Any Generation Resource:

(a)	A combined-cycle facility shall be considered a single Generation Resource; or.

(b)	Each unit of a combined-cycle facility will be considered a single Generation Resource if the combustion turbine and the steam turbine can operate separately, as stated in the Resource Registration on the Market Information System (MIS) Public Area.

(4)	With any single Generation Resource unavailable, and with any other generation preemptively redispatched, the contingency loss of a single facility, comprised of transmission line, auto transformer, or other associated pieces of equipment (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause the following:

(a) 	Cascading or uncontrolled Outages;

(b)	Instability of Generation Resources at multiple plant locations; or

(c) 	Interruption of service to firm demand or generation other than that isolated by the transmission facility, following the execution of all automatic operating actions such as relaying and Special Protection Systems (SPSs).

Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., RAPs) such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.