ROS Report

	NOGRR Number
	114
	NOGRR Title
	Synchronization with NPRR540, Clarification of Credible Single Contingency

	Timeline
	Normal
	Action
	Recommended Approval

	Date of Decision
	September 12, 2013

	Proposed Effective Date
	November 1, 2013

	Priority and Rank Assigned
	Not applicable.

	Nodal Operating Guide Sections Requiring Revision
	2.2.2, Security Criteria

2.7.2, Maintaining Voltage Profile

4.3, Operation to Maintain Transmission System Security

4.3.2, Real-Time and Short Term Planning

6.2.2, Design and Operating Requirements for ERCOT System Facilities

	Protocol Sections Requiring Revision
	2.1, Definitions

6.5.7.1.10, Network Security Analysis Processor and Security Violation Alarm

6.5.9.3.2, Advisory

6.5.9.3.4, Emergency Notice

	Revision Description
	This Nodal Operating Guide Revision Request (NOGRR) revises the use of Credible Single Contingency to align with actual practice and with Nodal Protocol Revision Request (NPRR) 540.

	Reason for Revision
	To align with NPRR540 and to respond to the 9/13/2012 ROS directive to the Network Data Support Working Group (NDSWG) and Operations Working Group (OWG) to modify the definition of Credible Single Contingency and apply the newly defined use to the Operating Guides.

	Procedural History
	· On 4/26/13, NOGRR114 was posted.

· On 5/15/13, OWG considered NOGRR114.

· On 5/31/13, an Impact Analysis was posted.

· On 6/14/13, CenterPoint Energy comments were posted.

· On 6/19/13, OWG considered the 5/15/13 OWG Report and Impact Analysis for NOGRR114.

· On 6/27/13, OWG again considered the 5/15/13 OWG Report and Impact Analysis for NOGRR114.

· On 7/11/13, ROS considered NOGRR114.

· On 7/30/13, ERCOT comments were posted.

· On 9/9/13, Constraint Management Plan Revision Request Workshop comments were posted.

· On 9/12/13, ROS again considered NOGRR114.

	OWG Decision 
	On 5/15/13, OWG was in consensus to recommend approval of NOGRR114 as submitted.

On 6/19/13, OWG was in consensus to table NOGRR114 until the 6/27/13 OWG meeting.

On 6/27/13, OWG was in consensus to endorse and forward the 5/15/13 OWG Report as amended by the 6/14/13 CenterPoint Energy comments and as revised by OWG, and the Impact Analysis for NOGRR114 to ROS.     

	Summary of OWG Discussion
	On 5/15/13, there was no discussion.

On 6/19/13, there was a request for NOGRR114 to be tabled to allow time for additional review of related issues.

On 6/27/13, there was no discussion.  

	ROS Decision
	On 7/11/13, ROS unanimously voted to table NOGRR114.  All Market Segments were present for the vote.

On 9/12/13, ROS unanimously voted to recommend approval of NOGRR114 as amended by the 9/9/13 Constraint Management Plan Revision Request Workshop comments.  All Market Segments were present for the vote.

	Summary of ROS Discussion
	On 7/11/13, there was no discussion.

On 9/12/13, there was no discussion.


	Business Case

	1
	· Aligns the Nodal Operating Guides with actual practice and with NPRR540.


	Sponsor

	Name
	Frank Owens on behalf of OWG

	E-mail Address
	fowens@crosstexas.com 

	Company
	Cross Texas Transmission LLC

	Phone Number
	(512) 276-6122

	Cell Number
	(512) 348-3294

	Market Segment
	Not Applicable


	Market Rules Staff Contact

	Name
	Kelly Landry

	E-Mail Address
	klandry@ercot.com

	Phone Number
	(512) 248-4630


	Comments Received

	Comment Author
	Comment Summary

	CenterPoint Energy 061413
	Endorsed current Nodal Operating Guide language regarding the use of Emergency Rating with Credible Single Contingencies and the requirement that ERCOT reduce loading to below the Normal Rating within two hours.    

	ERCOT 073013
	Proposed clarifications to Section 4.3.

	Constraint Management Plan Revision Request Workshop 090913
	Endorsed NOGRR114 as amended by the 7/30/13 ERCOT comments and as revised by the workshop.


	Comments


Please note that the baseline Operating Guide language in Section 6.2.2 has been updated due to the incorporation of NOGRR107, Disturbance Monitoring Requirements Clarifications, into the June 1, 2013 Nodal Operating Guides.

Please also note that NOGRR110, Synchronization with NPRR529, Congestion Management Plan, also proposes revisions to the following sections:

· Section 4.3.2

· Section 6.2.2

	Revised Proposed Guide Language


2.2.2
Security Criteria

(1)
Technical limits established for the operation of transmission equipment shall be applied consistently in planning and engineering studies, Congestion Revenue Rights (CRRs), Day-Ahead studies, Real-Time security analyses, and operator actions.
(2)
ERCOT shall operate the system such that pre-contingency flows are within applicable Transmission Facility Ratings.
(3)
ERCOT shall operate the system such that, unless an Emergency Condition has been declared by ERCOT, the occurrence of a Credible Single Contingency will not cause any of the following conditions: 

(a)
Uncontrolled breakup of the ERCOT Transmission Grid;

(b)
Loading of Transmission Facilities  above defined Emergency Ratings that cannot be eliminated in time to prevent damage or failure following the loss through execution of a Constraint Management Plan (CMP);

(c)
Transmission voltage levels outside system design limits that cannot be corrected through execution of a CMP before voltage instability or collapse occurs; or

(d)
Customer Outages, except for Load that is included in a CMP, high set interruptible and radially served Loads.

2.7.2
Maintaining Voltage Profile

ERCOT has the responsibility for monitoring and controlling the Voltage Profile and should use the following:

(a)
Operations Engineering

(i)
All voltage limits must be based on sound engineering studies that use the appropriate Network Operations Model.  TSP study results should be made available to ERCOT; and

(ii)
Transfer limits shall reflect voltage and/or reactive restrictions.

(b)
Coordination

(i)
Entities must coordinate high voltage limits in order to guarantee that the maximum continuous over-voltage of equipment is not exceeded.  Transmission Operators (TO) shall notify ERCOT of normal operating voltage limits and post-contingency voltage limits for each bus; 

(ii)
Low voltage limits must be coordinated in order to prevent one Entity from being a burden to another;

(iii)
Voltage limits shall not be violated during all normal and Credible Single Contingency conditions; and

(iv)
The operation of all Reactive Power devices under the control of a TO or a Qualified Scheduling Entity (QSE) will be coordinated under the direction of ERCOT to maintain transmission voltage levels within normal limits and post-contingency voltages within post contingency limits.  Static reactive devices will be managed to ensure that adequate dynamic reactive reserves are maintained at all times.

(c)
Notification

(i)
Generation Resources with voltage problems shall notify the TO to whom they are directly connected.  TOs shall notify other affected TOs and ERCOT; and

(ii)
ERCOT will monitor events and may direct actions to solve the problem.
(d)
Response

(i)
When the voltage levels deviate from established limits, ERCOT or the TO shall take immediate steps to relieve the condition using all available reactive resources.

(e)
Monitoring

(i)
TOs shall provide telemetry to ERCOT on all major transmission bus voltages.  

(f)
Controls

(i)
ERCOT must be aware of the location of and availability of reactive capability;

(ii)
ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows; and

(iii)
Controls to maintain Voltage Profiles may include but are not limited to capacitor switching, reactor switching, auto-transformer tap changing, generator reactive dispatch, transmission line switching, and Load shedding.

(g)
Documentation

(i)
Each TO must maintain a voltage/reactive plan for normal and Emergency Conditions and will provide this plan to adjacent TOs as well as ERCOT upon request.

(h)
Emergency or Abnormal Conditions

(i)
Transmission systems shall be designed so that effective reactive reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions;

(ii)
Major transmission lines shall be kept in service during light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded; and

(iii)
Voltage reduction should not be done on the transmission system unless coordinated with adjacent TOs.

4.3
Operation to Maintain Transmission System Security










(1)
ERCOT shall continue to operate according to Security Criteria outlined in Section 2.2.2, unless an Emergency Condition has been declared by ERCOT.


(2)
Transmission Overload – ERCOT can:

(a)
Order adjustment to unit generation schedules, switching of Transmission Elements or Load interruption to relieve the overloaded Transmission Element;

(b)
Order a Transmission Element whose loss would not have a significant impact on the reliability of transmission system switched out to increase interconnected system transfers.

(3)
Violation of security criteria – ERCOT can order changes to unit dispatch or commitment to eliminate or avoid a security criteria violation.  Normally these changes should be performed through market control mechanisms including Security Constrained Economic Dispatch (SCED) or Reliability Unit Commitment (RUC) as described in the Protocols, but if an ERCOT Operator finds these mechanisms insufficient to resolve the violation, the Operator may require any other action necessary to address the violation.

(4)
Partial Blackout or Blackout – ERCOT shall implement Black Start procedures.
4.3.2

Real-Time and Short Term Planning

ERCOT will conduct Real-Time and short term planning based on the security criteria established in these Operating Guides.  Operations during Forced and Planned Outages will also follow these criteria.  Line ratings are provided to ERCOT in accordance with Protocols and these Operating Guides.  ERCOT will employ congestion management, SPSs, RAPs and transmission switching schemes to facilitate the market use of the ERCOT Transmission Grid while maintaining system security and reliability in accordance with ERCOT and NERC Reliability Standards.  ERCOT will address operating conditions under which the reliability of the ERCOT System is inadequate and no solution is readily apparent in accordance with the Protocols and these Operating Guides.

6.2.2

Design and Operating Requirements for ERCOT System Facilities

(1)
Protective relay systems shall be designed to provide reliability, a combination of dependability and security, so that protective relay systems will perform correctly to remove faulted equipment from the ERCOT System.

(2)
For planned ERCOT System conditions, protective relay systems shall be designed not to trip for swings which do not exceed the steady-state stability limit (note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered).  Protective relay systems shall not interfere with the operation of the ERCOT System under the procedures identified in the other sections of these Operating Guides.

(3)
Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

(4)
The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even as a result of a Credible Single Contingency conditions.

(5)
Applicable Institute of Electrical and Electronic Engineers (IEEE)/American National Standards Institute (ANSI) guidelines shall be considered when applying protective relay systems on the ERCOT System.

(6)
The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to these Operating Guides or to accepted IEEE/ANSI practice, then the Facility owners affected shall negotiate a solution.

 (7)
The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

(8)
Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with the operating characteristics of any generating equipment protective relay systems or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

(9)
Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and protective relay systems.

(10)
Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Upon ERCOT’s request, within 30 days, Generation Entities shall provide documentation of coordination.

(11)
Special Protection Systems (SPSs) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action, other than the isolation of faulted elements, to provide acceptable ERCOT System performance.  SPS actions include, but are not limited to, changes in Demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable facility loadings.  An SPS does not include under-frequency or Under-Voltage Load Shedding (UVLS).  

(a)
A “Type 1” SPS is any SPS that has wide-area impact and specifically includes any SPS that:

(i)
Is designed to alter generation output or otherwise constrain generation or imports over Direct Current Ties (DC Ties); or 

(ii)
Is designed to open 345 kV transmission lines or other lines that interconnect Transmission Service Providers (TSPs) and impact transfer limits.  

(b)
A “Type 2” SPS is any SPS that has only local-area impact and involves only the Facilities of the owner-TSP.  The determination of whether an SPS is Type 1 or Type 2 will be made by ERCOT upon receipt of a description of the SPS from the SPS owner.  Any SPS, whether Type 1 or Type 2, shall meet all requirements of the NERC Reliability Standards relating to SPSs, and shall additionally meet the following ERCOT requirements:

(i)
The SPS owner shall coordinate design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources and DC Ties;
(ii)
The SPS shall be automatically armed when appropriate;

(iii)
The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, the SPS owner may provide a Real-Time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one or more of the SPS monitored Facilities exceeds 90% of the flow necessary to arm the SPS.  The cost necessary to provide such status indication shall be allocated as agreed by the SPS owner and the Generation Resource owner;

(iv)
The status indication of any automatic or manual arming/activation or operation of the SPS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owners of any Facility(ies) controlled by the SPS; and

(v)
When a TSP removes an SPS from service, the TSP or its Designated Agent shall immediately notify ERCOT Operations.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS and notify the market via the Market Information System (MIS) Public Area.  When a SPS is returned to service, the TSP or its Designated Agent shall immediately notify ERCOT Operations.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

(vi)
The status indication of the following items shall be provided by SCADA telemetry provided by the owner of the SPS equipment to ERCOT for incorporation into ERCOT systems:

(A)
Any automatic or manual arming/activation or operation of the SPS;

(B)
The in-service/out-of-service status of the SPS; and

(C)
Any additional related telemetry that already exists pertinent to the monitoring of the SPS (e.g. status indication of communications links between associated SPS equipment and TSP control center, arming limits of associated SPS equipment).
(12)
The owner(s) of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

(a)
ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS at least every five years as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and posted on the MIS Secure Area.

(b)
For a proposed Type 1 SPS, the review must be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Network Operations Model Change Request (NOMCR) to ERCOT.

(c)
For a proposed Type 2 SPS, the SPS may be placed into service before completion of the ERCOT review, with advanced prior notice to ERCOT in the form of a NOMCR.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  Existing SPSs that have already undergone at least one review shall remain in service during any subsequent review, and proposed modifications to existing SPSs may be implemented, upon notice to ERCOT, and approval of ERCOT before completion of the required ERCOT review.

(d)
The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of any Facility(ies) controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

(e)
An ERCOT SPS review shall verify that the SPS complies with the ERCOT Protocols, NERC Reliability Standards and these Operating Guides.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within 30 days.

(f)
As part of the ERCOT review and unless judged to be unnecessary by ERCOT, the appropriate Reliability and Operations Subcommittee (ROS) working groups such as the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and/or the System Protection Working Group (SPWG) shall review the SPS and report any comments, questions, or issues to ERCOT for resolution.  ERCOT may work with the owner(s) of Facilities controlled by the SPS as necessary to address all issues.

(g)
ERCOT shall develop a methodology to include the SPS in Security-Constrained Economic Dispatch (SCED), Outage Coordination, and Reliability Unit Commitment (RUC).

(h)
ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.
(13)
SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report located in Section 8, Attachment B, Relay Misoperation Report.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

(a)
ERCOT shall report all SPS operations and misoperations to the Texas Reliability Entity (Texas RE) for review.  SPS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to Texas RE.  An operation and misoperation of an SPS with respect to reporting requirements to Texas RE occurs when changes to the transmission system occur, including, but not limited to circuit breaker operation.  Owners of SPSs will provide a monthly report to ERCOT by the 15th of each month, for the previous month, describing each instance an SPS armed/activated and reset.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to Texas RE.

(b)
If an SPS which removes generation from service, operates more than two times within a six month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

(14)
For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the MIS Secure Area.  Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, using a NOMCR, whenever the SPS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all Facilities controlled by the SPS.
�Please note that NOGRR110 also proposes revisions to this section.


�Please note that NOGRR107 and NOGRR110 also propose revisions to this section.





114NOGRR-10 ROS Report 091213
Page 1 of 12
PUBLIC


