Methodology for Implementing Operating Reserve Demand Curve (ORDC) to Calculate Real-Time Reserve Price Adder

Effective ---------------------, 2014

Version _0.1

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 09/19/2013 | 0.1 | Initial draft | ERCOT Staff |

PROTOCOL DISCLAIMER

This document describes ERCOT systems and the response of these systems to Market Participant submissions incidental to the conduct of operations in the ERCOT Texas Nodal Market and is not intended to be a substitute for the ERCOT Protocols (available at http://www.ercot.com/mktrules/nprotocols/current), as amended from time to time.  If any conflict exists between this document and the Protocols, the Protocols shall control in all respects.

Table of Contents

1.	Purpose	1

2.	Background	1

3.	Real-Time Co-Optimization of Energy and Ancillary Services	2

4.	Interim Solution B+	2

5.	Methodology for Implementing ORDC	4

5.1.	Determine VOLL	5

5.2.	Determine LOLP	5

5.2.1.	Calculation of RS and RSNS	8

5.2.2.	Calculation of  and  	10

5.3.	Determination of Price Adder	11

6.	Methodology Revision Process	11

7.	Appendix 1: Parameters for Implementing ORDC	12

8.	Appendix 2: Interim Solution B+ Theory	13

8.1.	An Approximation Foundation for an ORDC	13

8.2.	ORDC for Multiple Reserves	16

8.3.	Determination of Price Adder Incorporating VNMA	20

# Purpose

Protocol Section 6.5.7.3, Security Constrained Economic Dispatch, requires the ERCOT Board to approve ERCOT’s methodology for implementing the Operating Reserve Demand Curve (ORDC) to calculate the Real-Time reserve price adders.  Additionally, the ERCOT Board must approve the parameters to be used in the methodology.

For each Security-Constrained Economic Dispatch (SCED) process, ERCOT calculates a Real-Time On-Line Reserve Price Adder (RTORPA) and a Real-Time Off-Line Reserve Price Adder (RTOFFPA) based on the On-Line and Off-Line available reserves in the ERCOT System and the ORDC.  The On-Line Reserve Price Adder is added to the Real-Time Locational Marginal Prices (LMPs) to determine the Real-Time Settlement Point Prices.  The price after the addition of RTORPA to LMPs approximates the pricing outcome of Real-Time energy and Ancillary Service co-optimization since RTORPA captures the value of the opportunity cost of reserves based on the defined ORDC.  An Ancillary Service imbalance Settlement is done based on Protocol Section 6.7.4, Real-Time Ancillary Service Imbalance Payment or Charge, to make Resources indifferent to the utilization of their capacity for energy or Ancillary Service reserves.

This document describes:

- the ERCOT Board-approved methodology that ERCOT uses for determining the Real-Time reserve price adders based on ORDC.

- the ERCOT Board-approved parameters for determining the Real-Time reserve price adders and effective date.

# Background

The concept of the “Interim Solution B+” was initiated by a paper by William Hogan, “Electricity Scarcity Pricing through Operating Reserves: An ERCOT Window of Opportunity,” which was filed with the Public Utility Commission of Texas (PUCT) by GDF Suez on November 14, 2012.  The paper emphasized the importance of an Operating Reserve Demand Curve (ORDC) in improving Real-Time scarcity pricing in the ERCOT market.  The proposed approach involved the Real-Time co-optimization of energy and Ancillary Services.

Preliminary analysis of the timeframe for implementing Real-Time co-optimization of energy and Ancillary Services indicated that it could not be done quickly.  ERCOT contacted Professor Hogan to determine the validity of modifying the existing energy offer floors as an interim solution.  This approach was labeled as “Interim Solution A.”  The resulting collaboration produced a calculation based on Loss of Load Probability (LOLP), Value of Lost Load (VOLL) and the level of available reserves in Real-Time, which was labeled as “Interim Solution B.”  Both interim solutions were presented and discussed at a PUCT workshop held on January 24, 2013.

During the January 24, 2013 workshop, concerns were raised about “Interim Solution B” in terms of negative market behavior that the proposal could incentivize.  To address these concerns, a modified approach was proposed, “Interim Solution B+,” which added an Ancillary Service imbalance Settlement to the “Interim Solution B” approach.  The Protocols require ERCOT to implement an ORDC without implementing Real-Time co-optimization of energy and Ancillary Services. This document describes “Interim Solution B+ as the methodology for developing the ORDC and the methodology for determining the reserve price adders using the ORDC.  It also lists the values of the parameters to be used.

# Real-Time Co-Optimization of Energy and Ancillary Services

Real-Time co-optimization of energy and Ancillary Services does result in the appropriate valuation of energy during periods when demand is high and operating reserves are low.  This valuation is accomplished through the utilization of an ORDC that results in the price of energy reflecting the opportunity cost of reserve scarcity.  The current ERCOT market includes co-optimization in its organized forward Day-Ahead Market (DAM) without an ORDC, while the Real-Time spot market does not include co-optimization of energy and Ancillary Services.  The Real-Time spot market only prices energy and does not include the opportunity cost of operating reserves.

The Real-Time energy and Ancillary Service co-optimization proposal utilizes ORDCs to create appropriate scarcity prices.  In the current ERCOT Real-Time spot market, demand is inelastic and energy and Ancillary Service co-optimization is not performed.  Resource energy offers or the administrative Power Balance Penalty Curve (PBPC) can set the price at or near the System-Wide Offer Cap (SWCAP) during scarcity conditions.  Presently, the SWCAP is the maximum price that a Resource can offer for energy.  The current SWCAP was set to $5,000/MWh on 6/1/2013, will be set to $7,000/MWh on 6/1/2014, and will be set to $9,000/MWh on 6/1/2015.  If Real-Time energy and Ancillary Service co-optimization is adopted, then the use of the SWCAP in Real-Time and its inter-relation with the PBPC and VOLL need to be revisited.  The design of the ORDC and the price of reserves under scarcity depend on the inter-relation between the PBPC, VOLL, ORDC and SWCAP.

Implementing Real-Time co-optimization requires Ancillary Service providers in the DAM to buy back Ancillary Services at the Real-Time price if such services are not provided in Real-Time.  Thus, a Real-Time Ancillary Service imbalance Settlement structure for reserves is a part of the Real-Time energy and Ancillary Service co-optimization solution.

# Interim Solution B+

Preliminary analysis of the timeframe for implementing Real-Time co-optimization of energy and Ancillary Services indicated that it could not be done in the near-term.  A “minimum” implementation of co-optimization would only co-optimize Responsive Reserve (RRS) Service with an estimated price tag of $25 million and a timeline of three to four years.  A “maximum” implementation would co-optimize RRS, On-Line Non-Spinning Reserve (Non-Spin) Service, Off-Line Non-Spin, Regulation Up (Reg-Up) Service  and Regulation Down (Reg-Down) Service with an estimated price tag of $42.5 million and a timeline of three to five years.

In order to provide a more gradual increase in the energy price, leading up to the SWCAP as conditions become scarce in Real-Time, two alternative approaches were proposed, “Interim Solution A” and “Interim Solution B.”  These approaches were filed with the PUCT on January 24, 2013 under Docket No. 40000, Commission Proceeding to Ensure Resource Adequacy in Texas [item# 369].

The “Interim Solution B” proposal removes the existing energy offer floor requirements from Generation Resources for Ancillary Service, and incorporates the ORDC into the determination of Real-Time prices for energy.  The proposal introduces a price adder to the system-wide energy price based on the ORDC, which is an increasing function that values the remaining reserves as a function of the total generation in the system.  While both approaches indicated above should create the desired effect of having a more gradual increase in the energy price as conditions become scarce in Real-Time, “Interim Solution B” provides a more accurate approximation of full Real-Time co-optimization of energy and Ancillary Services and will include prices for both energy and Real-Time reserves.

During the January 24, 2014 workshop, concerns were raised about “Interim Solution B”.  These concerns, which focused on negative market behavior that the proposal could incentivize due to the inconsistency between the increased prices and the Dispatch from the Real-Time market, included:

- Resources ignoring Dispatch Instructions to “chase” the higher energy prices;

- Entities reducing Real-Time energy offers to values below costs in order to offset possible inconsistencies with the DAM; and

- Entities needing to buy back DAM energy awards in Real-Time at a higher cost due to the potential inconsistencies.

The utilization of an Ancillary Service imbalance Settlement was developed to address these negative incentives.  The “Interim Solution B” combined with the Ancillary Service imbalance Settlement is what is being referred to as “Interim Solution B+.”

There are two key values that are part of “Interim Solution B+.”  The first value is a price for Real-Time reserves from Load Resources providing RRS and Resources that are participating in SCED.  This price serves as the price adder for the Real-Time energy price.  In order to address price inconsistency between the Dispatch and the final price, the remaining reserves provided by Resources minus their Ancillary Service obligation are paid this price adder as well.  The second value is the price calculated and used in the Ancillary Service imbalance Settlement for Real-Time reserves that are being provided by Off-Line Resources.  These are Resources that are not currently available for Dispatch by SCED but could be started from a cold temperature state in 30 minutes.  The Ancillary Service imbalance Settlement will ensure that Resources are indifferent between providing energy and reserves in Real-Time.  This addresses the earlier discussed incentive concerns.

While the incentive concerns were originally raised in regards to “Interim Solution B,” it is important to recognize that similar concerns also existed with the energy offer floors there were in place and modified as part of “Interim Solution A.”  This is specifically true for those Resources which are providing On-Line Non-Spin in Real-Time that have a marginal cost lower than $120/MWh.  Such a Resource has the incentive to ignore Dispatch Instructions in order to “chase” the higher energy price whenever the price is greater than their marginal cost.  However, an Ancillary Service imbalance Settlement process may be less feasible under an energy offer floor approach due to there not being an explicit price for Real-Time reserves.

There are two approaches to implementing an ORDC:

Approach 1:   If we assume that the SWCAP is the same as VOLL, then the maximum price on the PBPC would be set to SWCAP + 1.  The Real-Time spot market clearing process uses the SCED application to dispatch Resources and set prices.  For each execution of SCED, the marginal offer from Resources providing reserves will be determined and the ORDC will be constructed as LOLP * (VOLL - Marginal-Offer-From-Resource-Providing-Reserves).  Since the last parameter in this equation is not a fixed value and could vary for each SCED execution, the Real-Time ORDC could vary for each SCED execution as well.  In short, this approach is needed with the current rules in order to ensure that power balance is given the highest priority.  This approach, which uses a modified ORDC for each SCED execution, can result in a reserve price that is near zero and an energy price near SWCAP under scarcity conditions.

Approach 2:  In this approach SWCAP is only applicable to the PBPC.  Resources can only offer up to a new, smaller offer cap value (SWCAP_NEW).  The maximum price on the PBPC will still be set to SWCAP + 1, but the ORDC will be calculated based on LOLP * (SWCAP – SWCAP_NEW).  Under this approach, scarcity prices will reach SWCAP and the reserve prices will not need to be decreased under scarcity conditions as they are under Approach 1.  This approach allows the ORDCs for Real-Time to be predefined for each time period of the day rather than for each SCED execution.  It also ensures that the prices for reserves are always increasing as they are depleted.  In this approach, under scarcity conditions, reserve prices approach (SWCAP – SWCAP_NEW) and the price for energy approaches SWCAP.

Though these two approaches create the same Real-Time energy prices, they create different reserve prices and have different system change requirements.  Even though, Approach 2 is a simpler implementation and has the effect of taking the scarcity component out of the Resource energy offers, Approach 1 is adopted to implement ORDC to be consistent with the current PUCT rules.

# Methodology for Implementing ORDC

Determining the following values is a major part of implementing ORDC to calculate Real-Time Reserve Price Adder:

- VOLL;

- LOLP;

- The Real-Time price for remaining reserves in the ERCOT System.

## Determine VOLL

The VOLL is a parameter for implementing the ORDC and shall be approved by ERCOT Board.

## Determine LOLP

The key part of “Interim Solution B+” is the determination of LOLP.  LOLP depends on many factors, including the probability of forced outages, probability of Load forecast error and probability of wind forecast error.  It could also be different for different times of the day and for different months of the year.  LOLP at a given reserve level can be interpreted as the probability of the occurrence of an event with a magnitude greater than that reserve level.  A minimum contingency level (X) is chosen in order to send an appropriate scarcity price signal to maintain reliability and stability of the system.  The LOLP for reserve levels below the minimum contingency level (X) will be set to one.  In addition, since ERCOT is at a higher risk of shedding firm Load when reserves fall near or below the minimum contingency reserve level, the LOLP curve is shifted to the right by the minimum contingency level (X) amount.  The LOLP curve for a given reserve level (R) is given as follows:

LOLP is determined by analyzing historic events defined as the difference between the hour-ahead forecasted reserves with the reserves that were available in Real-Time during the Operating Hour.  These events are split into twenty-four groups, comprising of four seasons and six time-of-day blocks per day.  These groups are used to determine twenty-four distinct normal probability distributions of the events, which will determine the LOLP for the corresponding season and time block.  The detailed logic for determining LOLP is described as below:

- For each Operating Hour in the study period, calculate the system-wide Hour-Ahead (HA) reserve using the snapshot of last Hourly Reliability Unit Commitment (HRUC) for the Operating Hour (at the end of Adjustment Period):

HA Reserve = RUC On-Line Gen COP HSL - (RUC Load Forecast + RUC DCTIE Load)

+ RUC Off-Line Gen COP OFFNS Responsibility + RUC On-Line Load COP Non-Spin Responsibility + RUC On-Line Load COP Reg-Up Responsibility + RUC On-Line Load COP RRS Responsibility

- For each SCED interval in the study period, calculate the system-wide available SCED reserve using SCED telemetry and solution as:

SCED Reserve = SCED On-Line Gen HSL-SCED Gen Base Point + SCED Off-Line Gen OFFNS Schedule + SCED On-Line Load Telemetry RRS Schedule + SCED On-Line Load Telemetry Reg-Up Responsibility + SCED On-Line Load Telemetry Non-Spin Schedule

- For each Operating Hour in the study period, calculate the hourly average system-wide SCED reserve by averaging the interval SCED reserve in step 2).

- For each Operating Hour in the study period, calculate the system wide Reserve Error as:

Reserve Error = HA Reserve – SCED Reserve (Hourly Average)

- For each Operating Hour in the study period, allocate it to the corresponding season and time block. All the hours will be split into 24 distribution groups developed for the analysis based on the Season and the time of day:

- 4 Seasons of

  - Winter (Months 12,1, 2),

  - Spring (Months 3,4,5),

  - Summer (Months 6,7,8) and

  - Fall (Months 9,10,11)

- 6 time-of-day blocks each consisting of 4 hours

- Calculate the mean ( and standard deviation ( for each of the twenty-four distinct LOLP distributions using the calculated Reserve Error in step 4).  The detail results for 2011 and 2012 are illustrated in Table 1.  This hourly error is normally distributed and hence  for a given value reserve level R can be calculated:

LOLPμ,σ,R=1−CDFμ,σ,R

Where  is the Cumulative Distribution Function of the normal distribution with mean  and standard deviation .

Table 1 LOLP distributions by season and time-of-day block for 2011 and 2012

| Season | For Hours | μ | σ |
| --- | --- | --- | --- |
| Winter (Month 12, 1, 2) | 1-2 and 23-24 | 185.14 | 1217.89 |
|  | 3-6 | 76.28 | 1253.93 |
|  | 7-10 | 136.32 | 1434.64 |
|  | 11-14 | -218.26 | 1441.00 |
|  | 15-18 | -53.67 | 1349.52 |
|  | 19-22 | -183.00 | 1129.31 |
| Spring (Month 3,4,5) | 1-2 and 23-24 | 245.76 | 1174.61 |
|  | 3-6 | 460.41 | 1313.46 |
|  | 7-10 | 348.16 | 1292.36 |
|  | 11-14 | -491.91 | 1332.05 |
|  | 15-18 | -253.77 | 1382.60 |
|  | 19-22 | -436.09 | 1280.47 |
| Summer (Month 6,7,8) | 1-2 and 23-24 | 374.88 | 1503.97 |
|  | 3-6 | 1044.81 | 1252.25 |
|  | 7-10 | 339.01 | 1679.70 |
|  | 11-14 | -695.94 | 1251.05 |
|  | 15-18 | -270.54 | 1284.96 |
|  | 19-22 | -730.33 | 1331.49 |
| Fall (Month 9, 10,11) | 1-2 and 23-24 | 15.90 | 1044.88 |
|  | 3-6 | 478.97 | 1014.02 |
|  | 7-10 | 322.65 | 1036.07 |
|  | 11-14 | -473.16 | 1293.83 |
|  | 15-18 | -422.21 | 1246.49 |
|  | 19-22 | -177.76 | 1231.14 |

### Calculation of RS and RSNS

is the reserves from Resources participating in SCED plus the RRS from Load Resources.  is equal to  plus the reserves from Resources that are not currently available to SCED but could be started from a cold temperature state in 30 minutes.

[VERSION 1 – Effective pending implementation of NPRR555:]

- is calculated based on SCED telemetry and solution as:

RS=1−DF∗HSLGEN−HSLIRR−HSLNUC−BPGEN−BPIRR−BPNUC+RRSLR+REGUPCLR

Where

- DF is the discount applied to the Real-Time High Sustained Limits (HSLs) of Generation Resources.

- HSLGEN and BPGEN are the system total SCED On-Line HSL and Base Points respectively.

- HSLIRR and HSLNUC are the system total SCED telemetered On-Line HSL of Intermittent Renewable Resource (IRR) and nuclear Resources respectively.  The IRRs in this formula exclude Synchronous Condenser Units having an RRS Ancillary Service Schedule.

- BPIRR and BPNUC are the system total SCED On-Line Base Points of IRR and nuclear Resources respectively.

- RRSNCLR is the system total SCED telemetered RRS Ancillary Service Schedules from Load Resources other than Controllable Load Resources.

- BPCLR is the system total SCED Base Points from Controllable Load Resources.

- LSLCLR is the system total SCED telemetered Low Sustained Limit (LSL) from Controllable Load Resources.

- NONSPINCLR is the system total SCED telemetered Non-Spin Ancillary Service Schedule from Controllable Load Resources.

- RRSLRis the system total SCED telemetered RRS Ancillary Service Schedules from all Load Resources.

- REGUPCLR is the system total SCED telemetered Regulation Up Ancillary Service Schedules from Controllable Load Resources

[VERSION 2 – Replaces Version 1 upon implementation of NPRR555:]

1)	 is calculated based on SCED telemetry and solution as:

RS=1−DF∗HSLGEN−HSLIRR−HSLNUC−BPGEN−BPIRR−BPNUC+RRSNCLR+BPCLR−LSLCLR−NONSPINCLR

Where

- DF is the discount applied to the Real-Time High Sustained Limits (HSLs) of Generation Resources.

- HSLGEN and BPGEN are the system total SCED On-Line HSL and Base Points respectively.

- HSLIRR and HSLNUC are the system total SCED telemetered On-Line HSL of Intermittent Renewable Resource (IRR) and nuclear Resources respectively.  The IRRs in this formula exclude Synchronous Condenser Units having an RRS Ancillary Service Schedule.

- BPIRR and BPNUC are the system total SCED On-Line Base Points of IRR and nuclear Resources respectively.

- RRSNCLR is the system total SCED telemetered RRS Ancillary Service Schedules from Load Resources other than Controllable Load Resources.

- BPCLR is the system total SCED Base Points from Controllable Load Resources.

- LSLCLR is the system total SCED telemetered Low Sustained Limit (LSL) from Controllable Load Resources.

- NONSPINCLR is the system total SCED telemetered Non-Spin Ancillary Service Schedule from Controllable Load Resources.

[VERSION 1 – Effective pending implementation of NPRR555:]

- is calculated based on SCED telemetry and solution as

RSNS=RS+1−DF∗HSLGENOFFNS+HSLGENOFF30+NONSPINLR

Where

- HSLGENOFFNS is the system total SCED telemetered HSL of Off-Line Generation Resources providing Non-Spin

- HSLGENOFF30 is the system total SCED telemetered HSL of Off-Line and available Generation Resources that can be started from a cold temperature state in 30 minutes.

- NONSPINLR is the system total SCED telemetered Non-Spin schedule from all Load Resources

[VERSION 2 – Replaces Version 1 upon implementation of NPRR555:]

2)	is calculated based on SCED telemetry and solution as

RSNS=RS+1−DF∗HSLGENOFFNS+HSLGENOFF30+NONSPINCLR

Where

- HSLGENOFFNS is the system total SCED telemetered HSL of Off-Line Generation Resources providing Non-Spin

- HSLGENOFF30 is the system total SCED telemetered HSL of Off-Line and available Generation Resources that can be started from a cold temperature state in 30 minutes.

- NONSPINCLR is the system total SCED telemetered Non-Spin schedule from Controllable Load Resources.

### Calculation of  and

and  are functions that describe the LOLP at various reserve levels.

- Calculation of Curve :

is a function of the Real-Time reserves that should be available in the first 30 minutes of the hour and is intended to capture the LOLP for that level of reserves.  The general equation for is:

Where

- X in this equation is a minimum contingency level and represents a level of reserves at which ERCOT may need to begin to shed firm Load.

- is the  function for the spinning reserve.

is different from the 60 minutes  in Table 1, which is calculated based on the hourly error analysis.  The reserves are classified into two categories; those that are being provided by Resources in SCED and Load Resources providing RRS and those that are being provided by Resources that are not currently available to SCED but could be started from a cold temperature state in 30 minutes.  Since the first reserve type is available immediately, those reserves are the only ones considered to be available to respond to any event that happens in the first 30 minutes of the hour.  All reserve types are then considered to be available to respond to events that happen in the second 30 minutes of the hour.  From the hourly error analysis, a mean ( and standard deviation (for the 60 minute  are determined for each of the different seasons and time blocks.  Because the error analysis is hourly, to capture the events within the first 30 minutes for , the  and  needs to be scaled to reflect the 30 minute timeframe, with :

So the  can be calculated based on the 60 minute  as follows:

==

24  curves is developed based on the season and the time of day.

- Calculation of Curve :

is a function of all the Real-Time reserves that can be expected to be available with the hour and is intended to capture the LOLP for that level of reserves based on events that happen in an hour.  The general equation for is:

This is similar to  but the key differences here are the types of reserves considered and the  and  that are used in calculating LOLP

- The total On-Line and Off-Line applies for the full change in net Load over the hour and there is no scaling adjustments needed for  and  in the   calculations

- Again, X in this equation is a minimum contingency level

Like , twenty-four individual curves are created for .

## Determination of Price Adder

Once LOLP is determined, the price  for reserves that are being provided by Load Resources providing RRS and Generation Resources participating in SCED and the price  for the reserves being provided by Off-Line Generation Resources not currently available to SCED but could be made available to SCED in 30 minutes can be calculated.   and  are functions of the LOLP at various levels of Real-Time reserves, the net value of Load curtailment, and time duration during which the reserves are available.  and  are determined as follows:

Where v represents the net value of Load curtailment and is calculated as the VOLL minus the marginal cost of energy.  Marginal cost of energy is subtracted from VOLL to reflect the scarcity value of the marginal dispatch capacity and to ensure that the final cost of energy does not go above the SWCAP.

# Methodology Revision Process

Revisions to this document shall be made according to the approval process as prescribed in Protocol Section 6.5.7.3, Security Constrained Economic Dispatch.

# Appendix 1: Parameters for Implementing ORDC

The definition and values of the parameters used in implementing ORDC are as follows:

| Parameter | Definition | Unit | Value |
| --- | --- | --- | --- |
| VOLL | Value of Lost Load | $/MWh | 9000 |
| X | Minimum level at which ERCOT may need to begin shedding firm Load | MW | 2000 |
| DF | A discount factor for Generation Resource HSLs |  | 1% |
| δ | Duration of the first interval of the hour when Non-Spin cannot avoid curtailments | Hour | 0.5 |

# Appendix 2: Interim Solution B+ Theory

The “Interim Solution B+” theory proposed by Dr. William Hogan is described in the following sections.

## An Approximation Foundation for an ORDC

This section summarizes a series of steps to approximate the full Real-Time energy and Ancillary Service co-optimization ORDC and be explicit about the inclusion of the costs of generation and reserves to produce the implied scarcity price.  Here the focus is on responsive reserves.  The various variables and functions include:

Assume that unit commitment is determined.  The stylized economic dispatch model includes an explicit description of the expected value of the use of reserves.  This reserve description allows for a one dimensional change in aggregate net load, , and an asymmetric response where positive net load changes are costly and met with reserves and negative changes in net load are ignored.  This model is too difficult to implement but it provides an interpretation of a set of assumptions that leads to an approximate ORDC.  Here we ignore minimum reserve requirements to focus on the expected cost of the reserve dispatch.

The central formulation treats net load change  and use of reserve,  , to avoid involuntary curtailment.  This produces a benefit minus cost of  and this is weighted by the probability .  This term enters the objective function summed for all non-negative values of .  The basic formulation includes:

(1)

This model accounts for all the uncertain net load changes weighted by the probability of outcome and allows for the optimal utilization of reserve dispatch in each instance.  This problem could produce scarcity prices that could differ across locations.

To approach the assessment of how to approximate reserves with a common scarcity price across the system, we need to further simplify this basic problem as follows:

- Treat the utilization of reserves as a one-dimensional aggregate variable.

- Replace the responsive reserve limit vector with a corresponding aggregate constraint on total reserves.

- Utilize an approximation of the cost function, , for the aggregate utilization of reserves, and further approximate the change in costs with the derivative of cost times the utilization of reserves.

This set of assumptions produces a representation for the use of a single aggregate level of reserves for the system:

(2)

This formulation provides a reasonably transparent interpretation of the implied prices.  Focusing on an interior solution for all the variables except , we would have locational prices related to the marginal benefits of load:

(3)

The same locational prices connect to the system lambda and the cost of congestion for the binding transmission constraints.

(4)

The locational prices equate with the marginal cost of generation-only plus the cost of scarcity when this generation is at capacity, which appears in the usual form.

(5)

The locational prices equate with the marginal cost of responsive generation and display the impact of reserve scarcity.  First, the impact of changing the base dispatch of responsive generation implies:

The second order term captures the effect of the base dispatch of responsive dispatch on the expected cost of meeting the reserve utilization.  This term is likely to be small.  For example, if we assume that the derivative is constant, then the second order term is zero.

When we account for the base dispatch of reserves, we have:

.

When accounting for utilization of the reserves, we have:

.

Let .  Then for .  Hence,

.

Combining these, we can rewrite the locational price as:

(6)

Equations (3) thru (6) capture our approximating model for aggregate responsive reserves.  Here.  The term  in (6) is the scarcity price of the ORDC.  If the second order terms in (6) are dropped, then the scarcity price is the only change from the conventional generation only model.  In practice, we would have to update this model to account for minimum reserve levels, non-spin, and so on, but these changes would be the same as the discussion where we included an estimate of in defining the net value of operating reserves .

Note that under these assumptions the scarcity price is set according to the opportunity cost using  for the marginal responsive Generation Resource in the base dispatch.  Depending on the accuracy of the estimate in , this seeks to maintain that the energy price plus scarcity price never exceeds the VOLL.

Providing a reasonable estimate for  could be done either as an (i) exogenous constant, (ii) through a two pass procedure, or (iii) approximately in the dispatch.  For example, a possible procedure would define the approximating cost function as the least unconstrained cost,

.

This information would be easy to evaluate before the dispatch.

## ORDC for Multiple Reserves

The ERCOT practice distinguishes several types of reserves.  Setting aside regulation, the principal distinction is between “responsive” reserves (R) and “non-spin” reserves (NS).  The ORDC framework can be adapted to include multiple reserves.  This section summarizes one such modeling approach and relates it to the co-optimization examples above.  The main distinction is that “responsive” reserves are spinning and have a quick reaction time.  These reserves would be available almost immediately and could provide energy to meet increases in net load over the whole of the operating reserve period.  By comparison, non-spin reserves are slower to respond and would not be available for the entire period.

The proposed model of operating reserves approximates the complex dynamics by assuming that the uncertainty about the unpredicted change in net load is revealed after the basic dispatch is determined.  The probability distribution of change in net load is interpreted as applying the change over the uncertain reserve period, say the next hour, divided into two intervals.  Over the first interval, of duration (), only the responsive reserves can avoid curtailments.  Over the second interval of duration (1-), both the responsive and non-spin reserves can avoid involuntary load shedding.

This formulation produces different values for the responsive and non-spin reserves.  Let v be the net value of load curtailment, defined as the value of lost load less the avoided cost of energy dispatch offer for the marginal reserve.  The interpretation of the prices of reserves,, is the marginal impact on the load curtailment times , the probability of the net change in load being greater that the level of reserves,.  This marginal value differs for the two intervals, as shown in the following table:

| Marginal Reserve Values |  |  |
| --- | --- | --- |
|  | Interval I | Interval II |
| Duration |  | 1- |
|  | 0 |  |

This formulation lends itself to the interpretation of Figure 2 where there are two periods with different demand curves and the models are nested.  In other words, responsive reserves  can meet the needs in both intervals and the non-spin reserves can only meet the needs for the second interval.

The resulting prices satisfy:

(7)

This formulation lends itself to a relatively easy implementation in the co-optimization model.

Figure 2

As shown later, the introduction of multiple types of ORDCs does not much affect the economic dispatch model for Real-Time.  The same properties apply to the interpretation of the effect of ramping limits.  If there are no ramping limits, then the energy dispatch and energy prices of the co-optimized model would also be optimal for the model that excludes reserves and simply optimizes the energy dispatch with the scarcity price for reserves added as a constant to all the generation offers.  But introduction of binding ramping limits would undo this simplicity.

One way to implement the two-step approximation is to assume different random draws for the two intervals from the distribution of net load change.  Suppose that there are two variables  representing the incremental net load change in the two intervals.  Further assume that the two variables have a common underlying distribution for a variable  but are proportional to the size of the interval.  Then, assuming independence and with  the net load change over the full two intervals, we have:

The implied variance of the individual intervals is derived from the impact of the square root law for the standard deviation of the sums of independent random variables.

Hence, for the first interval, the standard deviation is , where  is the standard deviation of the net change in load over both intervals.  With this adjustment, the revised version of (7) becomes:

(8)

Here the different distributions refer to the net change in load over the first interval, and over the sum of the two intervals.  The distribution over the sum is just the same distribution for the whole period that was used above.

There would be an adjustment to deal with the minimum reserve to meet the max contingency.  The revised formulation would include:

Returning to the approximation of simultaneous co-optimization of energy and reserves with an ORDC, the key connection is in the design of the function , derived from the ORDC.  Recall that with   and .  Everything else would stay the same in the approximating model, with the optimal level of reserves determining the scarcity opportunity cost of responsive generation as:

The resulting dispatch model, the approximation of equation (2) would be.

(9)

This formulation ignores the second order impacts of the effect on reserve prices.

## Determination of Price Adder Incorporating VNMA

One issue that arises is the assumption that net Load changes in excess of the reserves above the minimum contingency levels would result in the equivalent of involuntary Load curtailment at the cost of VOLL.  This is an approximation that includes setting a value for various non-market interventions that would precede literal Load curtailment.  If the value is approximately VOLL for all these actions, then the simple one-step approximation should suffice.  However, it is possible to extend the argument to include different values for different actions.

For example, suppose we assume there is a two-step approximation.  The first step of capacity  accounts for interventions   whose opportunity cost is the Value of Non-Market Actions (VNMA).  Here we assume that VNMA < VOLL.  Only after these actions are taken do we get to the second step of actions that are literal or functional equivalents of Load curtailment valued at VOLL.

The LOLP curves used in the two-step approach are shown as below:

Where:

RS are the reserves available in the first 30 minutes

RSNS are the reserves available in the full 60 minutes including Off-Line Resources that could be started from a cold temperature state in 30 minutes

XLL is the minimum level at which ERCOT may need to begin shedding firm Load

XNMA is the minimum level at which ERCOT may need to begin taking non-market actions

LOLPS is a curve for the probability of shedding Load calculated considering the reserve

NMAPS is a curve for the probability of non-market actions considering the reserve

forecast error over a 30 minute period.  These curves use the same error analysis but are shifted by different amounts due to the difference between XLL and XNMA

LOLPSNS is a curve for the probability of shedding Load calculated considering the reserve

forecast error over a 60 minute period

NMAPSNS is a curve for the probability of non-market actions considering the reserve

forecast error over a 60 minute period.  These curves again use the same error analysis but are shifted by different amounts due to the difference between XLL and XNMA.

The calculation of πSLL,πSNMA,πNSLLandπNSNMAis similar to the calculation of πSand πNSwhich is described in Section 5.3 Determination of Price Adder without VNMA.  With VNMA, PS and PNS are determined as follows:

Where

VOLL is the Value of Lost Load

VNMA is the Value of Non-Market Actions

vLL=max (0, VOLL- Marginal Offer)

vNMA=max (0, VNMA-Marginal Offer)

It can be observed that if vNMA is set as 0, the calculated values of PS and PNS incorporating VNMA will be equal to the calculated value of PS and PNS without VNMA. The current implementation of ORDC and determination of PS and PNS is done without VNMA

W. Hogan, “Electricity Scarcity Pricing through Operating Reserves: An ERCOT Window of Opportunity,” Mossavar-Rahmani Center for Business and Government, Harvard Kennedy School, November 1, 2012, available at http://www.hks.harvard.edu/fs/whogan/Hogan_ORDC_110112r.pdf.