| NOGRR Number | 111 | NOGRR Title | Synchronization with NPRR527, Required Combined Cycle Telemetry for Operational Awareness and PDCWG Analysis |
| --- | --- | --- | --- |

| Date | September 17, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Bill Blevins |
| E-mail Address | bblevins@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6691 |
| Cell Number |  |
| Market Segment | Not applicable. |

Comments

ERCOT submits these comments in response to the concerns raised at the 8/21/13 Operations Working Group (OWG) meeting.  These comments clarify the performance analysis and exceptions related to frequency disturbances.

Revised Proposed Guide Language

- 2.2.8	Performance/Disturbance/Compliance Analysis

(1)	Performance/Disturbance/Compliance analysis shall be performed by ERCOT for the purpose of ensuring conformance with the Protocols.  All Generation Resources and Controllable Load Resources, except nuclear-powered Resources or Wind-powered Generation Resources (WGRs) with a permanent exemption approved by ERCOT, must respond to frequency disturbances with a Governor droop of 5% or less.  When assessing conformance with the Protocols, ERCOT shall exclude from the performance analysis the following instances of a Generation Resource or Controllable Load Resource:

(a)	Operating within the larger of 5MW or 2% of the  High Sustained Limit (HSL) for low frequency disturbances;

(b)	Operating within the larger of 5MW or 2% of the Low Sustained Limit (LSL) for high frequency disturbances;

(c)	Carrying spinning capability only comprised of non-frequency responsive power augmentation equipment; or

(d)	Having a technical or physical limitation filed with and approved by ERCOT.

(2)	ERCOT may utilize the Performance Disturbance Compliance Working Group (PDCWG) as a technical resource in providing input for types of technical or physical limitations that may be approved by ERCOT.

(3)	ERCOT shall make a regular report on selected system disturbances, documenting the response of individual  Generation Resources and Controllable Load Resources.  In addition, Resource Entities, QSEs, and individual members of the PDCWG are encouraged to work within their respective companies to enhance the performance of individual  Generation Resource’s or Controllable Load Resource’s control systems through application of the results of the PDCWG studies.