## Slide 1: Ancillary Services Methodology Changes
Bill Blevins
Manager, Operations Planning

## Slide 2: Schedule for discussion with Stakeholders
Week of 30th Sept | Release the red-line version to stakeholders
7-Oct | QMWG
9-Oct | WMS
10-Oct | ROS
7-Nov | TAC
18-Nov | BOD

## Slide 3: Proposed Changes
Update the factors used to adjust the Regulation Service quantities for additional installed wind generation
Remove Load Forecast Bias from determination of Non-Spinning Reserve Service (NSRS) capacity

## Slide 4: Regulation Service Adjustment for Additional Wind
Quantity of Regulation Service for each hour is based on the required Regulation Service from the previous month and the same month of the previous year
Additional installed wind generation will tend to add to the quantity of Regulation Service required; The 2008 GE Study has previously been used to adjust the required quantity of Regulation as new wind capacity was added
Study was completed with data from 2005-2006
  Not much wind data
  Wind data was generated by AWS Truewind

## Slide 5: Regulation Service Adjustment for Additional Wind
ERCOT has updated the analysis from the GE study using actual wind output and uses the median of the regulation requirement for the last five years.
Conclusions:
  Relationships between Reg needed and MW wind is still linear
  Overall, increase in Reg needed per MW increase in installed wind is slightly less than what GE Study predicted
MW Changes in Regulation requirements are small; less than 5MW in any hour
Link for Report on study to update the GE table
http://www.ercot.com/calendar/2013/10/20131007-QMWG

## Slide 6: Relationship between Reg Requirements and Wind Capacity
Chart: Wind Capacity (MW)
| 0 | 5000 | 10000 | 15000
GE Morning (0700-1000) | 386 | 421 | 452 | 486
ERCOT Morning (0700-1000) | 387.1 | 404.73 | 409.66 | 411.91 | 416.44 | 420.39 | 423.86
Morning (0700-1000)
Chart: Wind Capacity (MW)
| 0 | 5000 | 10000 | 15000
GE Mid-Day (1400) | 255 | 264 | 283 | 298
ERCOT Mid-Day (1400) | 261.51 | 269.52 | 274.44 | 275.69 | 278.5 | 282.04 | 285.7
Mid-Day (1400)
Chart: Wind Capacity (MW)
| 0 | 5000 | 10000 | 15000
GE Evening (1800) | 232 | 265.5 | 319 | 384
ERCOT Evening (1800) | 248.5 | 252.64 | 254.62 | 256.14 | 260.01 | 261.11 | 266.07
Evening (1800)
Chart: Wind Capacity (MW)
| 0 | 5000 | 10000 | 15000
GE Night (2300) | 36 | 40 | 47 | 53
ERCOT Night (2300) | 53.06 | 55.32 | 57.87 | 57.95 | 59.08 | 61.49 | 65.58
Night (2300)

## Slide 7: Reg Difference between using GE tables and updated tables
Notes: Suggests that the regulation requirements are driven by LOAD, not wind

## Slide 8: NSRS Load Forecast Bias - Background
The NSRS Load Forecast Bias was originally implemented during the Zonal market due to perceived over-commitment (RPRS) by ERCOT based on day-ahead forecast
  The day-ahead forecast, on average, may be biased toward the high side, since it is generally accurate on most days but may be significantly high on a relatively few days when unpredicted rain occurs
  The “compromise” at the time the bias calculation was introduced into the A/S Methodology was that the load forecast would be reduced by the bias but the amount of NSRS would be increased by the same amount
  With the addition of HRUC, ERCOT is now able to wait until closer to the Operating Hour to issue commitments, which provides QSEs the latitude to self-commit Resources in lieu of receiving an HRUC instruction

## Slide 9: MTLF Model Comparisons - unbiased
Notes: Mean average day-ahead load forecast error is low
Zonal is about the same since 2009.
  Added Meteorologist to operations to help select

## Slide 10: Day-Ahead Daily Peak Model Error
A few hours result in an “average” bias
Notes: Every 5000 MW due to rain error will create 20 MW calculated bias for the entire block of Hours 5000/240.

## Slide 11: Example of large forecast error – June 9, 2013
Day-Ahead weather forecast did not account for cooler temperatures
Results in a large contribution to the bias

## Slide 12: Day-Ahead Daily Peak Model Error
High load hours – no bias
Notes: Note* If the calculation was performed using only the 5 highest peak days for August and September, the results would have been 0 MW of bias.

## Slide 13: 2 hour ahead Daily Peak Model Error (actual – predicted)
Little or no bias

## Slide 14: 4 hour ahead Daily Peak Model Error (actual – predicted)

## Slide 15: Problems with Current Implementation of Bias in Forecasting
The bias is calculated based on the day-ahead error and applied not only to the Day Ahead load forecast but to the Real-Time load forecast as well.
  The load forecast becomes more accurate as the time of the forecast approaches real-time
The bias is applied to all three ERCOT load forecasts regardless of which forecast was actually used in determination of bias
The posting of unbiased forecast and/or biased forecast has created communication issues for ERCOT with external entities.

## Slide 16: August Day-Ahead Daily Peak Forecasts
For August:
Peak Forecast Error w/o bias (Predicted- Actual)
A3: 1,082 MW
A6: 1,182 MW
ERCOT: 81 MW
Bias at peak was 545 MW
Peak Forecast Error including Bias (Predicted-Bias- Actual)
A3: 537 MW
A6: 637 MW
ERCOT: (464) MW
Bias results in ERCOT’s best forecast being low by 464 MW at peak.
Accurate forecast was available
Notes: Selecting a forecast that is obviously too low during high-load conditions is problematic for System Operators

## Slide 17: Overall NSRS Cost Savings
If Load Forecast Bias was not applied to NSRS procurement, ERCOT would have saved
  Cost Savings for Non-Spin = (original MCPC * original AS plan) – (original MCPC * new AS plan)
This is true savings, since the offset would be for RUC commitments for capacity which rarely occur

## Slide 18: RUCs for Capacity
Notes: NPRR-382 and 383 report for RUC
NPRR-401 self-commitment
NPRR-402 self commitment between DAM and RUC
NPRR-416 buy back and removal of claw back
NPRR-435 RUC offer curves
NPRR-442 RUC of RMR at CAP

## Slide 19: QMWG Discussion
Some Market Participants had concerns about removing the load forecast bias completely from the AS Methodology
Suggestions were made to continue using the bias that looks at load forecast error that matches HRUC timeline.
Suggestions were also made about not including some of the rainy days when calculating the load forecast bias
There was general consensus that, the Control Room should use unbiased and most accurate Load Forecast

## Slide 20: ERCOT’s Recommendation
ERCOT recommends stakeholders to endorse the revised Ancillary Services Methodology which removes the load forecast bias adjustment from the Non-Spin Reserve procurement quantity and replaces the GE tables used to adjust the Regulation Service quantities for incremental wind additions with updated tables.