## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: September Meeting
Met Sept 26, 2013
  18 members representing 12 companies as well as ERCOT & TRE.
NPRR 486/ SCR 773 – update
Event review
GREDP update
Frequency Control Report Sept 2013

## Slide 3: NPRR 486/ SCR 773 update
Reviewed SCR773 in an open forum with WebEx
Focus on development of metric(s) to track effect of the SCR
Additional questions

## Slide 4: NPRR 486/ SCR 773 cont
Questions:
  What operator actions or interventions are occurring?
  If operator actions are occurring what is frequency and severity of the intervention?

## Slide 5: NPRR 486/SCR773
Metrics
Trend and monitor the regulation deployed by hour
Set target of 50 MW for total regulation deployed by hour
Set target of 85% for the number of intervals where regulation deployment was both up and down on peak(zero crossing)
Follow protocols for target f <1.2% exhaustion rate for all hours
Using a 50MW filter, target 15 occurrences per month for regulation bias in consecutive 5 minute intervals

## Slide 6: FRRS data and deployment review
Recommend proportional response/deployment
Option 2: Adjust the granularity for deployment to 3 steps
  Parameter changes are needed to add the extra granularity
  Near term solution
  ERCOT working to implement this change

## Slide 7: Event Review
PDCWG Reviewed 5 events
  Event resulted in good system frequency performance with few poor performers identified
  Non Frequency responsive RRS providers were noted and ERCOT will follow up with QSEs regarding their performance

## Slide 8: GREDP
All Conventional Generators passed metric
Increase in Wind Resource control performance
  With CREZ lines being energized there are less curtailments
  Scores have stayed consistent
  Signals better control of Wind Resources that are being curtailed

## Slide 9: ERCOT Frequency Control Report September 2013
Sydney Niemeyer NRG Energy
October 1, 2013

## Slide 10: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.
ERCOT total Time Error Correction time is from NRG data.
CPS 1 & 2 from NRG frequency data.

## Slide 13
CPS1 12 Month Rolling Average = 167.37

## Slide 18
60.010 <= HZ < 60.015

## Slide 22
Time Correction History

## Slide 25
ERCOT Primary Frequency Response – BAL-003-1
2014 Bias and Frequency Response Measure

## Slide 29: Focus for 2013
Formal & documented review/report of frequency responsiveness for Power Augmentation on Combined Cycle Resources (train not individual unit)
Review regulation/GTBD deployment effectiveness (SCR 773)
  Study the impact of HSL/basepoint/generation deviation on compliance and reliability
Pilot of fast frequency response – characterize & create evaluation process.
Ancillary Service Overhaul (new)
  No performance required for nonpayment (freq. resp AS)
Responsive Reserve requirements, qualification vs. compliance. (10min vs. 16 second)
Standardized/consistent metrics for PFR analysis (BAL001-TRE).
  Work on realistic measurement of combined cycles
Standardized/reasonable expectations for extreme events (2750MW or larger lost) – driven by NERC.
ERS impact review with appropriate ERCOT group. Target Q1-2014
PMU data understanding of implications
Red = Work on going
Check = completed goal

## Slide 30
Questions?