| NOGRR Number | 111 | NOGRR Title | Synchronization with NPRR527, Required Combined Cycle Telemetry for Operational Awareness and PDCWG Analysis |
| --- | --- | --- | --- |

| Date | August 20, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Bill Blevins |
| E-mail Address | bblevins@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6691 |
| Cell Number |  |
| Market Segment | Not applicable. |

Comments

In light of the 7/17/13 OWG recommendation regarding Nodal Operating Guide Revision Request (NOGRR) 111, ERCOT submits these comments to propose revisions which exclude Resources from frequency deviation analysis when technical justification for the submitted operating limits have been approved by ERCOT.  ERCOT also recommends that Wind-powered Generation Resources (WGRs) with permanent exemptions should be excluded from the frequency deviation analysis.

Additionally, Attachment A, Primary Frequency Response Reference Document, of the pending Regional Reliability Standard, BAL-001-TRE-1, Primary Frequency Response in the ERCOT Region, addresses the 5 MW / 2% language and therefore should be removed from the NOGRR as there could be potential conflict with the Regional Standard as it is pending Federal Energy Regulatory Commission (FERC) approval.  If the FERC approves the Regional Reliability Standard, then it will be the effective guideline and therefore not required in the Operating Guides.

Revised Proposed Guide Language

- 2.2.8	Performance/Disturbance/Compliance Analysis

(1)	Performance/Disturbance/Compliance analysis shall be performed by ERCOT for the purpose of ensuring conformance with the Protocols.  All Resources, except nuclear-powered Resources or Wind-powered Generation Resources (WGRs) with a permanent exemption approved by ERCOT, must respond to frequency disturbances with a Governor droop of 5% or less unless limited by a High Sustained Limit (HSL) or other operating limits filed with and approved by ERCOT.

(2)	ERCOT shall make a regular report on selected system disturbances, documenting the response of individual  Resources.  In addition, Resource Entities, QSEs, and individual members of the Performance Disturbance Compliance Working Group (PDCWG) are encouraged to work within their respective companies to enhance the performance of individual  Resource control systems through application of the results of the PDCWG studies.