| NOGRR Number | 124 | NOGRR Title | Additional VRT Requirement for IRRs |
| --- | --- | --- | --- |

| Date | October 16, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Jeff Billo / Shun-Hsien (Fred) Huang |
| E-mail Address | Jeff.Billo@ercot.com / shuang@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6334, (512) 248-6665 |
| Cell Number |  |
| Market Segment | ERCOT |

Comments

ERCOT submits these comments to address several concerns voiced by affected parties and by stakeholders participating in the September 18, 2013 meeting of the Operations Working Group.  First, ERCOT deletes references to “voltage-related equipment,” and clarifies that the requirement applies only to new WGRs.  Underlying this approach is the conclusion that the replacement of turbines or other equipment on grandfathered WGRs should not trigger the higher HVRT standard unless the turbine replacement amounts to a new WGR under paragraph (9) of Section 3.10.7.2, Modeling of Resources and Transmission Loads.

Second, this comment proposes that a WGR would be exempted from the new HVRT requirement only if it had synchronized with the ERCOT System before August 30, 2013, rather than simply having signed an Interconnection Agreement by that date.  While this change increases the sweep of this NOGRR, ERCOT believes this necessary to avoid creating a loophole that would allow developers that signed an IA before the grandfather date to later change the turbine model.

Third, this comment restates the HVRT requirement in a new paragraph, rather than simply leaving it in the caption of the graphic illustrating the requirement.  In this new paragraph, ERCOT also clarifies that the voltage used to determine compliance with the High Voltage Ride Through (HVRT) requirement is measured at the IRR’s Point of Interconnection (POI), consistent with the existing Low Voltage Ride Through requirement.

Revised Cover Page Language

None.

Revised Proposed Guide Language

2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources

(1)	All Intermittent Renewable Resources (IRRs) shall also comply with the requirements of this Section, except as follows:

(a)	An IRR that initially synchronizes with the ERCOT System before August 30, 2013 is not required to meet any high VRT requirement greater than 1.1 per unit voltage.  However, any WGR that initially synchronizes with the ERCOT System on or after August 30, 2013 shall be VRT-capable in accordance with all VRT requirements in this Section.

(b)	An IRR that interconnects to the ERCOT System pursuant to an SGIA executed prior to November 1, 2008 is not required to meet VRT requirements presented in this Section.  However, any WGR that is installed on or after November 1, 2008 and that initially synchronizes with the ERCOT System before August 30, 2013 (except for a WGR installed pursuant to an SGIA executed before November 1, 2008) shall be VRT-capable in accordance with the low VRT requirements in this Section and high-voltage requirements in this Section up to 1.1 per unit voltage.  Any WGR that initially synchronizes with the ERCOT System on or after August 30, 2013 shall be VRT-capable in accordance with all VRT requirements in this Section.

(c)	Notwithstanding any of the foregoing provisions, an IRR’s VRT capability shall not be reduced over time.

(2	)	Each IRR shall provide technical documentation of VRT capability to ERCOT upon request.

(3)	Each IRR is required to set generator voltage relays to remain in service for at least 0.15 seconds during all transmission faults and to allow the system to recover as illustrated in Figure 1, Default Voltage Ride-Through Boundaries for IRRs, below.  Recovery time to 90% of per unit voltage should be within 1.75 seconds.  Faults on individual phases with delayed clearing (zone 2) may result in phase voltages outside this boundary but if the phase voltages remain inside this boundary, then generator voltage relays are required to be set to remain connected and recover as illustrated in Figure 1.

(4)	Each IRR shall remain interconnected during three-phase faults on the ERCOT System for a voltage level as low as zero volts with a duration of 0.15 seconds as measured at the Point of Interconnection (POI) unless a shorter clearing time requirement for a three-phase fault specific to the generating plant POI is determined by and documented by the TSP in conjunction with the SGIA.  The clearing time requirement shall not exceed nine cycles.

(5)	Each IRR shall set generator voltage relays to remain interconnected to the ERCOT System during the following high-voltage conditions, as illustrated in Figure 1: 1.2 per unit voltage for up to 0.2 seconds, 1.175 per unit voltage for up to 0.5 seconds, and 1.15 per unit voltage for up to 1.0 seconds.  The indicated voltages are measured at the POI.

(6)	An IRR may be tripped Off-Line after the fault clearing period if this action is part of an approved Special Protection Systems (SPSs).

(7)	VRT requirements may be met by the performance of the generators; by installing additional reactive equipment behind the POI; or by a combination of generator performance and additional equipment behind the POI.  VRT requirements may be met by equipment outside the POI if documented in the SGIA.

(8)	If an IRR fails to comply with the clearing time or recovery VRT requirement, then the IRR and the interconnecting TSP shall be required to investigate and report to ERCOT on the cause of the IRR trip, identifying a reasonable mitigation plan and timeline.

Figure 1:  Default Voltage Ride-Through Boundaries for IRRs.