## Slide 1: Final Report Weather Sensitive Emergency Response Service (WS ERS) Pilot Project
Carl Raish, ERCOT
Technical Advisory Committee
November 7, 2013

## Slide 2: Background
ERCOT Board approved WS ERS Pilot Project in March 2013 to test an ERS product with demand reduction capability that varies based on weather.
WS ERS Pilot Features:
  Dispatched as early as EEA Level 1
  Fleet-wide testing of Pilot Resources – 8 tests (2 per month)
  Maximum of 8 actual EEA deployments
  Maximum 3-hour duration for a deployment
  Paid based on actual performance with accelerated reductions to discourage over-offering
  QSE allowed to increase or decrease number of sites each month within specified limits
Procured for June 2013 through September 2013 Contract Period
Pilot cost – approximately $111k
ERCOT Public
November 7, 2013
Notes: <number>

## Slide 3: Pilot Purposes
Evaluate the ability of weather-sensitive Loads to provide dispatchable demand response during summer system conditions
Evaluate the accuracy of Qualified Scheduling Entity (QSE) projections of demand response capabilities and Load growth
Evaluate deployment impacts on end-use customers
Identify any unforeseen challenges in procuring, deploying and evaluating the performance of weather-sensitive Loads
ERCOT Public
November 7, 2013
Notes: <number>

## Slide 4: 1. Evaluate Demand Response Capability
WS ERS MW offers based on normalized peak conditions
2 Loads procured
  1 Residential Load – 2.5 MW
  1 Non-Residential Load – 0.1 MW
Fleet MW Reductions
  Average over 8 tests – 1.78 MW
  Range 1.39 – 2.35 MW)
  QSE deployment issues affected test results on all but last test
  If the deployment issues had been avoided, the fleet likely would have met offer
Payment reductions would be imposed
  Based on performance alone QSE would have received 68.4% of full payment
  Because of low performance, an accelerated reduction would be imposed and QSE would receive 48.5% of full payment
ERCOT Public
November 7, 2013

## Slide 5: 2. QSE Projection of Growth
6 Loads submitted through Resource ID Phase of Procurement
  2 Loads rejected by ERCOT for failing WS qualification standards
3 Loads offered by 2 QSEs
  2 Residential and 1 Non-Residential
  1 Residential offer rejected on reasonableness of bid criteria
Population growth during Contract Period
  Residential Load increased from 1,238 to 2,355 sites
  Projected sites 1,950
  Non-Residential Load increased from 29 to 64 sites
  Projected sites 35
ERCOT Public
November 7, 2013

## Slide 6: 3. Impacts on End-use Customers
Survey questionnaire has been designed and is being administered by the QSE
Survey results not available at this time … results will be reported to Demand Side Working Group when complete
ERCOT Public
November 7, 2013

## Slide 7: 4. Unforeseen Challenges – Lessons Learned
Participating DR Provider discovered and corrected flaws in their deployment system
Third-party access to advanced meter interval data is important to effectively manage these types of demand response programs
Payment reduction provisions are effective in creating an incentive for DR Providers to submit achievable offers and to address identified performance issues
ERCOT test procedures refined
Performance calculations revised to address identified issues
ERCOT Public
November 7, 2013