## Slide 1
Overview of Revised Ancillary Services (AS) Framework Proposal
Dan Woodfin, Julia Matevosyan, Sandip Sharma, Fred Huang
ROS
November 14, 2013

## Slide 2: Drivers for new AS Framework
Current AS Framework has performed well but has issues
  Resources could provide some services more efficiently if the requirements were decoupled (PFR/ FFR/ Contingency Reserve)
  New service needed to ensure technical requirements are met that used to be provided, inherently, by generators (e.g. inertia)
  Awkward to fit capabilities of new technologies (e.g. CCGTs with duct firing, wind turbines) that could provide services efficiently
  Changes in market design and control systems(e.g. 5 minute dispatch, HRUC) have reduced the need for other services
  New regulatory requirements (BAL-003)
Need for changes has been highlighted in discussion of Fast Responding Regulation Service (FRRS), NPRR 524(Resource Limits in Providing Ancillary Service), etc.
Notes: Slide #5

## Slide 3: Goal
Current AS Framework
Based on capabilities of conventional steam generating units
Unique services bundled together due to inherent capabilities of conventional units
Mix of compensated and uncompensated services
New technologies are cobbled on, with difficulty
Future AS Framework
Technology neutral
Market-based
Based on fundamental needs of the system, not resource characteristics
Unbundled services
Flexible for new technologies
Pay for performance, where practical
Co-optimized procurement
Will evolve over time
5+ Years
Now
Transition Plan TBD
Notes: This is key slide

## Slide 4: Scope of Proposed AS Framework
Long-term Ancillary Services (AS) framework intended to guide:
  Decisions on near-term changes to current AS
  Requirements for changes to ERCOT systems (EMMS, etc.)
  Investment in new resources and new resource types by the mkt.
Framework will be developed in phases, due to complexity of issues
  Current Phase will only address frequency control services
  Future Phases may address Voltage Support and other services
Framework should eventually include roadmap for transition from current AS to future framework
  Prioritization of services to be transitioned
  Inter-relationship of services that must transition concurrently
  High-level consideration of ERCOT systems and market impacts

## Slide 5: ERCOT Proposal
  ERCOT proposes the transition to the following five AS products:
  Synchronous Inertial Response Service (SIR),
  Fast Frequency Response Service (FFR),
  Primary Frequency Response Service (PFR),
  Regulating Reserve Up (RRU) and Regulating Reserve Down (RRD) Service, and
  Contingency Reserve Service (CR).
  This revised AS set adds and/or redefines specific AS products currently used by the ERCOT System and
  Subsumes different elements within the current Responsive Reserve Service into several of the newly defined services.
  Recognizes during the transition period from today’s AS to the future AS set, there may be the need for a Supplemental Reserve Service that would be similar to today’s 30-minute Non-Spin Service.

## Slide 6: Synchronous InertiaL Response(SIR) service

## Slide 7: Synchronous Inertial Response (SIR) Service, Purpose
SIR is stored kinetic energy that is extracted from the rotating mass of a synchronous machine following a disturbance in a power system
Maintain minimum Rate of Change of Frequency (RoCoF)
Provide sufficient time from Point A to Point C, for Fast Frequency Response and Primary Frequency Response
No triggering RoCoF protection of synchronous generators (generally 0.5 Hz/s)

## Slide 8: Synchronous Inertial Response Service, Need
  SIR has significant implications on the RoCoF during power imbalances;
  With increasing use of non-synchronous generation, changing load characteristics (less motor loads), increase in Combined Cycle units (lower inertia), the system SIR response is reduced:
    RoCoF increases, leaving insufficient time for PFR to deploy and arrest the system frequency excursion.
    High RoCoF may trigger generation RoCoF protection, tripping additional synchronous generators.

## Slide 9: Synchronous Inertial Response Service, Need
  So far, the RoCoF during high wind/low load condition was less than 0.2 Hz/s and the average time to reach frequency nadir during frequency events is 4 to 6 seconds.
  The system inertia available in the real time operations under current conditions is still sufficient.
  Studies based on 2012 system conditions indicated RoCoF as high as 0.4 Hz/s for two largest unit trip (2750 MW as per recently approved NERC BAL-003 standard).

## Slide 10: SIR, Future work
  Monitor and project the trend of ERCOT system inertial response and RoCoF
  Identify the minimum needs of system inertia and duration between points A and C
  Gather data to determine each generator’s RoCoF tolerance
  Investigate capability and value of synthetic inertial response from renewable energy resources to contribute to system’s SIR

## Slide 11: Fast frequency response (ffr) service

## Slide 12: Fast Frequency Response (FFR) Service
  Need
To changing frequency to supplement the inherent inertial response from synchronous machines
To provide sufficient time for PFR to deploy and arrest fast frequency excursion in the event of sudden power imbalance
  Deployment and Performance
Self deployment
Provide full response within 30 cycles (0.5 secs.) at a specified frequency thresholds and sustained for at least 10 minutes
FFR service will require a high resolution measurement

## Slide 13: Fast Frequency Response (FFR) Service
  Discussion
Presently there is no separate FFR Service in ERCOT, however up to 1400 MW of Responsive Reserve Service (RRS) procured from Load Resources (LR) satisfy FFR characteristics
In the proposed AS framework FFR and PFR are highly interdependent and the required quantity of each service can vary based on the system conditions
FFR and PFR work together to produce the desired system response
FFR service cannot completely replace the PFR service
A performance requirement needs to developed

## Slide 14: Primary frequency response (Pfr) service

## Slide 15: Definition of PFR Service
Primary Frequency Response (PFR) is defined as the instantaneous proportional increase or decrease in real power output provided by a Resource in response to system frequency deviations.
  This response is in the direction that stabilizes frequency.
  Primary Frequency Response is attained due to Governor or Governor-like action
  PFR is instantaneous response relative to the frequency deviation,
  PFR is generally delivered completely within 12 to 14 seconds.

## Slide 16: Primary Frequency Response (PFR) Service- Need
ERCOT as a single Balancing Authority Interconnection with only limited interconnection to the other Interconnects is solely responsible for maintaining frequency to maintain reliability and meet NERC standard requirements.
  All of ERCOT’s frequency response can only come from Resources within the ERCOT Interconnection.
  On July 18th, 2013 FERC issued a Notice of Proposed Rule Making (NOPR) approving the BAL-003 NERC Frequency Response Standard
  BAL-003 sets a Frequency Response Obligation (FRO) for each BA based on loss of two largest single units.
  The minimum FRO for ERCOT is 286 MW/0.1 Hz

## Slide 17: Determination of the Amount of FFR and PFR Reserves
The objective of Fast Frequency Response (FFR) and Primary Frequency Response (PFR) Reserves should be to ensure Frequency is arrested above UFLS threshold of 59.30 Hz and to meet NERC FRO Standard (BAL-003).
Frequency Response Obligation (FRO) for ERCOT is determined based on instantaneous loss of two largest units (2750 MW).
ERCOT must develop methodologies for the regular assessment of the needed concurrent amounts of both FFR and PFR.

## Slide 18: Determination of the Amount of FFR and PFR Reserves
How much PFR is needed will be based on minimum requirement for FFR while maintaining minimum PFR capability within Generators (for example, in the current RRS, Load Resources can provide up to 50% of 2800 MW RRS).
System Load | FFR | PFR(5% Droop)
<=35000 MW | 840 MW(30% 0f 2800) | 1960 MW
<=35000 MW | 0 MW | 4480 MW

## Slide 19: Regulating Reserve (rr) service

## Slide 20: Regulating Reserve (RR) Service – Up & Down
An amount of reserve responsive to Load Frequency Control, which is sufficient to provide normal regulating margin.
ERCOT generation is dispatched through Security Constrained Economic Dispatch (SCED) every five minutes to balance the generation and demand. The power imbalance between each SCED interval will cause frequency deviation that requires Regulating Reserve to compensate. This action will be provided by RR service.

## Slide 21: Regulating Reserve (RR) Service – Up & Down
While not substantially changing from todays Regulation Service ERCOT is proposing to implement the following:
  LFC signals will be delivered by ERCOT to the QSE specifically for the Resource providing this service
  The deployment instructions should be determined by taking into consideration ramp rates, HSLs etc. of each of the individual Resources.
  Resources providing RR should be limited to min(NURR,NDRR)*5*0.70, where NURR and NDRR are Normal-Up Ramp Rate and Normal-Down Ramp Rate
  The pay for performance approach should reward those Resources that closely follow the ERCOT LFC signal
  ERCOT will re-visit its LFC and RLC to avoid deploying RR for more than 10 continuous minutes in one direction during normal operation.

## Slide 22: Contingency reserve (cr) service

## Slide 23: Contingency Reserve (CR) Service – Need & Purpose
CR is to ensure that the Balancing Authority is able to restore Interconnection frequency within defined limits following a DCS event or large net load forecast error within 15 minutes and restore its Primary Frequency and Regulating Reserve.
According to NERC BAL-002-1 Disturbance Control Standard (DCS), The minimum amount of CR required is equivalent to “Most Severe Single Largest Contingency”, in ERCOT’s case this is currently 1375 MW.
ERCOT may additionally procure CR reserve to cover for large net load forecast errors.
To ensure ERCOT can meet the standard, the CR must be fully deliverable within 10 minutes so that frequency can be restored to the pre-disturbance level within 15 minutes

## Slide 24: Contingency Reserve
  Qualification
Resources providing CR should be qualified up to the MW value to which they are able to ramp within 10 minutes from the time of deployment.
  Deployment
ERCOT will deploy CR for a sizable generation trip.
Resources providing CR must telemeter their ramp-rates such that SCED can dispatch the full Resource CR responsibility within 10 minutes.
  Performance
Resources providing CR must be able to deliver and sustain the reserve deployments for the full hour it is carrying that obligation.

## Slide 25: Supplemental reserve (Sr) service

## Slide 26: Supplemental Reserve (CR) Service
SR service is needed to compensate for net load forecast error and/or forecast uncertainty on days in which large amounts of reserve are not available online
Generation Resources capable of being ramped to a specified output level within thirty (30) minutes or Load Resources that are capable of being interrupted within thirty (30) minutes and that are capable of running (or being interrupted) at a specified output level for at least one (1) hour
Supplemental Reserve Service would be similar to today’s 30-minute Non-Spin Service

## Slide 27: End

## Slide 28: Synthetic IR
Inverter based resources can have the capability to inject active power into the system initiated through control system action following a disturbance, e.g. generator trip.
This capability, so called synthetic inertia, is already available from several WTG manufacturers.
Synthetic inertia capability requires control action in response to falling system frequency and therefore is not equivalent to synchronous machine inertia
However synthetic inertia will improve RoCoF and help to arrest system frequency decay. More discussion and evaluation of synthetic inertia performance is required.

## Slide 29: Synthetic IR, example from Hydro-Quebec