ERCOT CONCEPT PAPER

Future Ancillary Services in ERCOT

Draft Version 1.1

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 09/27/2013 | 1.0 | Initial Public Draft | ERCOT |
| 11/01/2013 | 1.1 | Incorporate Oct-24 Workshop feedback | ERCOT |

Table of Contents

Executive Summary	5

Rethinking ERCOT’s Ancillary Services	8

1.	Introduction	8

2.	New Resource Characteristics	9

3.	New Regulatory Requirements	10

4.	Need to Maintain System Frequency and Capacity Reserves	11

5.	Proposed Type of Services	12

6.	Synchronous Inertial Response (SIR) Service	15

Need for SIR Service	15

Purpose of SIR Service	15

Synthetic SIR Service	16

Market Construct for SIR	17

Transition and Implementation Considerations for SIR	18

7.	Fast Frequency Response (FFR) Service	19

Need for FFR Service	19

Purpose of FFR Service	19

Market, Transition and Implementation Considerations Associated with FFR	20

8.	Primary Frequency Response (PFR) Service	20

Need for PFR Service	20

Definition of PFR	20

Governor Setting Requirement for Generation Resources	21

Resource Limit On Carrying PFR	21

Determination of Amount of FFR and PFR Reserve Needed	22

Market Construct for FFR and PFR	23

Transition and Implementation Considerations Associated With FFR and PFR	24

9.	Regulating Reserve (Regulation) Service (Up & Down)	25

Need for Regulating Reserve Service (Up & Down)	25

Purposed changes for Regulation Service (Up & Down)	25

Market Construct for Regulation (Up & Down)	26

Transition and Implementation Considerations Associated with Regulation (Up & Down)	26

10.	Contingency Reserve (CR) Service	26

Need for CR Service	26

Purpose of CR Service	27

Qualification of Resources for CR Service	27

Performance Measurement of Resources Providing CR	27

Market Construct for CR	27

11.	Supplemental Reserve (SR) Service	28

Need for SR Service	28

Purpose of SR Service	28

Qualification of Resources for SR Service	28

Performance Measurement of Resources Providing SR	28

Market Construct for SR	28

12.	Global Market, Transition and Implementation Considerations of New AS	29

13.	Summary of the Proposed Ancillary Services	30

References	36

# Executive Summary

Over the years, ERCOT has been successful in complying with the North American Electric Reliability Corporation (NERC) standards with the Ancillary Services (AS) that it has procured and deployed.  For example, ERCOT’s average monthly Control Performance Standard (NERC CPS1) scores have consistently been around 165% over the last year, which is a clear indication that ERCOT is performing extremely well in controlling frequency.  Other performance measures also reflect that the ERCOT AS construct currently in place has served ERCOT well from a reliability and secure operations perspective.

In the summer of 2012, as ERCOT began discussing a pilot project to investigate a new Fast Responding Regulation Service (FRRS), several discussion items surfaced that suggested that ERCOT should “rethink” the entire existing set of AS.  The following are some of the reasons that have motivated ERCOT to explore improvements and changes to the current AS approach in ERCOT:

- The current AS construct was fork-lifted from the market design developed in the late 1990’s and did not necessarily anticipate some of the changes that have taken place and the changes likely to occur in the near future.

- Today’s generation mix in ERCOT is different from the mix that existed 15 years ago.

- Some of the new Resources expected to be added to the ERCOT system bring with them additional challenges and at the same time, some of them bring with them new capabilities in providing AS.

- New regulatory requirements are on the horizon.

- A new AS approach will better utilize the capabilities of the existing and new resources and will allow ERCOT to more efficiently provide the expected reliable and secure operations.

- Improved procurement methods of AS, improved specifications of performance for Resources providing AS and the implementation of “pay for performance” settlement methods (similar to those outlined in FERC Order 755) will lead to a more efficient way to acquire and deploy AS.

This concept paper reviews the AS needs based on likely changes expected to occur in ERCOT and proposes a framework for a new Ancillary Services set to address these changes, as well as guidance for the transition from the existing AS framework.

The scope of the concept paper is limited to those physical aspects of operations related to frequency control that are currently addressed by the Regulating, Responsive Reserve and Non-Spin AS.  Emergency Response Service, Voltage Support, Reliability Must-Run (RMR) units and Black Start Services are not in scope at this time.

The transition will require revisions to the Nodal Protocols and changes to the current ERCOT Operation, Market and Settlement systems.  This paper is intended to provide a starting point for discussions among ERCOT Staff, the IMM, the Reliability Monitor, the PUCT and the ERCOT Market Stakeholders to achieve a consensus plan of action for addressing future AS needs, their procurement and settlement.  Ultimately, this consensus is expected to be reflected in the final version of this paper and provide the basis for the revisions and changes to Nodal Protocols and ERCOT Operations, Market, and Settlement and Billing Systems.

Implicit in ERCOT’s analysis is the fact that ERCOT is a stand-alone interconnection and wholesale electricity market. This means that ERCOT is a single-Balancing Authority (BA) Interconnection – in NERC terms – and it cannot generally rely on any neighboring BA’s (in the Eastern and Western Interconnections) when responding to system events and emergencies (e.g. a loss of large amounts of generation, weather initiated events etc.).

ERCOT is recommending the transition to the following six AS products:

- Synchronous Inertial Response Service (SIR),

- Fast Frequency Response Service (FFR),

- Primary Frequency Response Service (PFR),

- Up and Down Regulating Reserve Service (Regulation) [the acronym “RR” is too confused with Responsive Reserve and should not be used here. Protocols use the term Regulation when meaning both services], and

- Contingency Reserve Service (CR).

- Supplemental Reserve Service (SR)

[how and on what timeline will the PUC chapter 25 rules be modified to account for the new ancillary services suggested here;  this seems to be a significant undertaking and will require a lot of time to litigate at the PUC.]

The revised AS set, as described in more detail below, adds and/or redefines specific AS products currently used by the ERCOT system; and, additionally, subsumes different elements within the current Responsive Reserve and Non-Spin Service into several of the newly defined services.    With the exception of the SIR service, ERCOT visualizes market procurement to be similar to the existing AS procurement markets.

While ERCOT believes that Supplemental Reserve Service (SR)  may not ultimately be needed in the long term, it will be needed during the transition from the AS set of today to the future AS set and for some period of time thereafter.  ERCOT proposes to implement Supplemental Reserve Service, that would be similar to today’s 30-minute Non-Spin Service.

ERCOT suggests that its system changes and upgrades related to the new AS product set be coordinated with its system maintenance and upgrade schedules concurrently with changes that may be required in the market participant systems. ERCOT also recommends that sufficient notice time be provided for market participants and for retail consumers to make adjustments to their forward wholesale and retail contracts.

As ERCOT and the Market Stakeholders proceed,  it may be determined that some of the new proposed AS may be required sooner than others (for example SIR) and that it may be best for the market if several services are grouped together and tied to the same commercial go-live date.  It is expected that any major transition to a new AS set would occur after a scheduled ERCOT EMS upgrade project and therefore may not be implemented until 2015 or 2016.

# Rethinking ERCOT’s Ancillary Services

## Introduction

The Electric Reliability Council of Texas (ERCOT) is an Independent System Operator (ISO) that serves over 23 million customers in Texas, and represents 85% of the state’s electric load. The Public Utility Regulatory Act of Texas designates ERCOT as the Independent System Operator and as such ERCOT operates the ERCOT interconnect transmission system and wholesale electricity market. As defined by NERC standards, ERCOT is a single-Balancing Authority (BA) Interconnection, which means it cannot generally rely on any neighboring BA’s for sole assistance during system events and emergencies.

With approximately 11,000 MW of installed wind capacity in the ERCOT market alone, Texas has the highest levels of installed wind generation capacity of any state in the United States and expects continuing growth of renewables in the foreseeable future. ERCOT’s load currently varies from a peak of slightly below 70 GW in the summer to minimum of 22 GW during off-peak seasons. The combination of huge seasonal variance in system load and high penetration of intermittent and variable renewable generation resources, such as wind generation, increases ERCOT’s operational challenges significantly. Nevertheless, ERCOT has been successfully operating the system with high wind penetration over the past years. ERCOT has developed unique expertise on wind generation capabilities, deliverability and impact of wind generation on power system, which, along with constantly improving wind power forecasting tools, allows ERCOT to better predict AS needs. ERCOT expects to utilize a similar approach as other intermittent and variable generation resources become an increasing share of the ERCOT resource set in the future.

In December 2010, ERCOT implemented the current ERCOT Nodal Market. In this market, resource scheduling and dispatch became resource-specific as opposed to the portfolio-based approach in the previous Zonal Market. This change has led to improved efficiencies in unit commitment and dispatch across the ERCOT system. The introduction of the Nodal Market was one of the key factors contributing to the successful integration of intermittent resources into the ERCOT system.  Resource-specific dispatch with 5-minute resolution allows ERCOT to closely follow net load variations and is one of the main reasons why ERCOT has been successful in integrating renewables with minimal increase in AS capacity.

The current AS framework for the ERCOT Region was designed when large steam generators were the predominant generation type in ERCOT.  These units have certain inherent characteristics and the Ancillary Services framework was designed around those characteristics.  This framework has gradually, but significantly, evolved as gas-fired combined cycle plants and wind generators have become larger portions of the generation mix. However, it has become more difficult and less efficient to continue with the current AS set while accommodating emerging technologies and the evolving capabilities of existing resources. The current effort to review ERCOT’s AS set is intended to ensure the continued reliability and security of the ERCOT system, taking into consideration existing and emerging technologies.

In the last decade new generation technologies have begun to appear, e.g. non-synchronous generation (wind and solar), as well as battery storage, connected to the ERCOT grid via power electronic inverters. These technologies have very different characteristics and performance compared to the conventional synchronous generation fleet. For example:

- Inverter based generation technologies and battery storage do not contribute to system inertia; and

- Solar and wind generation are intermittent in nature and power output cannot be accurately predicted.

On the other hand, the frequency response provided by a battery or wind generator is controlled by the inverter electronics and has the potential to respond faster than that of conventional generators.  ERCOT has strived to propose a revised AS framework that is based on the fundamental needs of the power system to maintain frequency control, is as neutral as possible to the technology types that are able to provide the services, and avoids unnecessary restrictions that limit the provision of the fundamental AS requirements by as broad a set of resources as possible.

## New Resource Characteristics

Many new synchronous generation resources use a technology where the generator/turbine mass is much smaller than historical boiler steam turbine generation that made up the majority of generation capacity when the current set of Ancillary Services were developed. Furthermore, the increasing penetration of non-synchronous resources leads to economic displacement of some synchronous generators that would otherwise be committed to serve a given load.  Because these non-synchronous resources are electrically connected to the system through an electronic inverter, these resources typically do not contribute inertia to the system, resulting in an overall reduction in the system inertia within the ERCOT Interconnection. However, ERCOT system generation capacity is significantly increasing that adds rotating mass to the Grid as well, but with the change in generation technology, inertial mass in aggregate is continuing to decrease.  Figure 1 shows the effect of declining grid inertia within ERCOT interconnection from 2006 to 2010. The Data Set I includes 43 historical events with an average wind generation of 1157 MW and an average 557 MW unit trip. The events in Data Set I include frequency disturbance events during the periods of January to May and October to December in years 2006 & 2007 and January to May of 2008. Data Set II consists of 44 historical events with an average wind generation of 2490 MW and an average 595 MW unit trip.  Data Set II includes frequency disturbance events during the periods of October to December of 2008, January to May and October to December of 2009 as well as January to April of 2010 [1].

Figure 1: Interpolated Inertial Frequency Response

This analysis shows a decline of system inertial response for the Data Set II (Red) compared to Data Set I (Blue) for the same type of events during similar system conditions with total on-line conventional generation capacity less than 35,000 MW, which results in larger frequency delta (Y-axis) for the same MW loss (X-axis).  The decline in Inertial Response  leads to faster frequency decay and lower frequency nadir during a generation resource forced outage (refer to Figure 2 below) as well as more severe changes in frequency due to normal load and generation variations. Additionally, the decline in Inertial Response will also result in larger frequency deviation for smaller unit trips and potentially trigger Under-Frequency Load Shed (“UFLS”) more often.

ERCOT currently estimates that the penetration of renewable resources has the potential to increase to as much as 16 GW within the next few years and may further increase in the longer horizon [2].  The displacement of synchronous generators as the result of the increased wind production has the potential to further reduce the system inertial response capability. The current AS set is not specifically designed to address this challenge.

## New Regulatory Requirements

The recently FERC approved NERC BAL-003 standard [4] requires each Balancing Authority to meet a minimum Frequency Response Obligation (additional detail on this standard is discussed below).  NERC also recently circulated a Reserve Policy guideline, which reaffirms its support for maintaining Frequency Responsive, Regulating and Contingency Reserves.  The Reserve Policy applies to ERCOT and the objective of this reliability guideline is to identify key practices and information on specific issues critical to maintaining the highest levels of Bulk Electric System reliability [3].

## Need to Maintain System Frequency and Capacity Reserves

This section describes the concerns and challenges for today’s AS products in the foreseeable future and identifies the need, from a system perspective, for AS related to system frequency and capacity reserves to maintain adequate system security and reliability.

Figure 2: Typical frequency response following a generator trip.

Following disturbances in a power system, all online synchronous machines provide Synchronous Inertial Response (SIR). This response has significant implications on the rate of change of frequency (RoCoF) during sudden power imbalances. With an increasing amount of non‐synchronous generation (e.g. wind generators) this response is reduced and RoCoF becomes higher, leaving insufficient time for other reserves to deploy and arrest the decline in system frequency before it drops to an unacceptable level [5].

As described in the following, the situation is complex and there are a number of factors that must be considered in the analysis of the system response and potential mitigating services. For example, with less synchronous generation online, there is a need for fast-acting response to changing frequency in the immediate post event time period. Fast Frequency Response (FFR) defined as active power response faster than the Primary Frequency Response (PFR) may, in the event of a sudden power imbalance, increase the time to reach the frequency nadir and mitigate the RoCoF, thus allowing sufficient time for PFR to respond [5].  Since ERCOT is a single BA Interconnection and is not synchronously connected with any other interconnections, ERCOT needs a PFR service to maintain stable frequency and meet NERC standard requirements. Additionally, recently approved NERC BAL-003 standard also requires ERCOT to meet minimum Frequency Response Obligation, which is based on instantaneous loss of two largest units (2750 MW).

Normal system operations require Regulating Reserves (Regulation) services to provide secondary frequency response and are used by the BA’s Load Frequency Controller to  maintain the frequency at nominal value (60 Hz.) by issuing signals every four seconds. Regulation is primarily needed to maintain good frequency control around the nominal frequency control point of 60 Hz and meet the NERC Control Performance Standard (CPS1). Each BA is required to maintain its rolling 12-month CPS1 Score higher than 100%. ERCOT’s current CPS1 score is above 165%. Generally, during contingency events, it is expected that both PFR and Regulation-Up will be deployed to recover from the event.

Additionally, NERC Standard BAL-002-1 Disturbance Control Standard (DCS) requires ERCOT to carry enough reserve to recover its Area Control Error (“ACE”) to pre-disturbance level, post DCS event, within 15 minutes.  In the NERC parlance, capacity reserves that are utilized for this purpose are referred to as Contingency Reserves.  The purpose of the Contingency Reserve is to ensure that the Balancing Authority (ERCOT) is able to restore Interconnection frequency within defined limits following a DCS event and restore its Primary Frequency and Regulating Reserve capacity to pre-disturbance level. In order for ERCOT to meet the requirements of the NERC Reliability Standard (BAL-002), ERCOT needs to identify its "Most Severe Single Contingency" to determine its minimum Contingency Reserve requirement.

## Proposed Type of Services

To continue to operate reliably and meet regulatory standards, ERCOT is proposing that it’s AS product set be revised to provide the following six types of AS:

- Synchronous Inertial Response Service (SIR),

- Fast Frequency Response Service (FFR),

- Primary Frequency Response Service (PFR),

- Up and Down Regulating Reserve Service (Regulation), and

- Contingency Reserve Service (CR).

- Supplemental Reserve Service (SR)

The deployment of the reserve categories represented by these six AS are governed primarily by NERC Reliability Standards including Regulating Reserve to meet the CPS1 Standard (BAL-001), Contingency Reserve to meet the DCS Standard (BAL-002) and Primary Frequency Response to meet the Frequency Response Obligation Standard (the newly FERC approved BAL-003 standard).  ERCOT is not a part of a NERC Reserve Sharing Group and therefore must maintain sufficient capacity within its boundaries to manage not only system contingencies but also the potential error in its operating Load Forecasts. As such, Supplemental Reserve Service which provides capacity to the Grid within 30 minutes and thus at potentially at a lower cost to consumers may be used to replace Contingency Reserves that may be depleted due to their use to manage a Load Forecast error.   How well ERCOT meets these reliability metrics also depends on the interaction of the proposed Synchronous Inertial Response Service and FFR.

The table below summarizes existing AS framework (left column) and proposed future AS framework (right column). For each service, the expected time to respond to a deployment signal and the time to deliver full deployed capacity is shown.  The last row of the table illustrates total make-up of current and proposed AS.

| Current Ancillary Services Framework | Future Ancillary Services Framework |
| --- | --- |
|  | Synchronous Inertial Response |
| Responsive Reserve Service from Load | Fast Frequency Response |
| Responsive Reserve Service from Generation and other Governor Reponse. | Primary Frequency Response |
| Regulating Reserve | Regulating Reserve |
|  | Contingency Reserve Service |
| Non-Spin | Supplemental Reserve Service |
| Make-up of current AS | Make-up of proposed AS |

Table 1: Existing and Proposed AS Frameworks

## Synchronous Inertial Response (SIR) Service

### Need for SIR Service

Synchronous Inertial Response has significant implications on the rate of change of frequency (RoCoF) during power imbalances.  With increasing non-synchronous generation SIR is reduced and RoCoF increases, leaving insufficient time for PFR to deploy and arrest system frequency decline[5], i.e. time between point A and C, Figure 2.  High RoCoF can cause frequency to reach the nadir faster and trigger under-frequency load shedding of firm load as a result and in extreme cases even higher RoCoF may also trigger generator’s RoCoF protection tripping.   There is therefore a need to assure the provision of a sufficient amount of inertial response on the ERCOT system.  SIR service is intended to meet this need.

### Purpose of SIR Service

Synchronous Inertial Response (SIR) is an instantaneous response that is continuously self-deployed from synchronous machines following disturbances and is a key determinant of the strength and stability of the power system.  Synchronous Inertial Response is defined as stored kinetic energy (at nominal frequency) that is extracted from the rotating mass of a synchronous machine following an imbalance in a power system. Stored kinetic energy is based on the commissioned design capability of the plant.  It can be determined through appropriate validation procedures based on the following relationship:

Stored kinetic energy = J(02/2=H·MVA,

- Where; the stored kinetic energy is in Mega Watt – Seconds;

- J is the combined moment of inertia of a synchronous machine and turbine prime mover in kg·m2, based on their size and weight;

- (0 is the nominal rotor speed in rad/s, and

- MVA is the machines rated capacity in Mega Volt – Amperes.

- H is the figure of merit used to analyze the synchronous machine’s inertial response and is referred to as the machine’s inertia constant in seconds.

Solving for H the above equation results in  H = J(02/(2·MVA) seconds.

The inertial response that a synchronous machine can provide is independent of the machine’s power output and the total system response to an initiating event is determined by the summation of the contributions from each of the online synchronous machines.  ERCOT will determine by analysis the desired response of the system under the largest generator trip event.  How much SIR ERCOT requires, will be based on fnadir>59.3 Hz., that is more than prevailing initial threshold of UFLS and RoCoF limitations implied by RoCoF protection settings of synchronous generators in ERCOT system.  The proposed constraint imposed on the unit commitment is that the summation of inertial contributions from each of the synchronous machines, committed for energy and AS, must achieve the required system inertial response.

Resource performance will be evaluated based on machine parameters (H and rated MVA) and machine status (online/offline) and every individual synchronous resource capable of providing this service will be required to provide ERCOT with  machine specific data (via the RARF) and telemetry of its on-line status.

As of July, 2013 ERCOT’s record for wind penetration as a percent of total instantaneous load is 35% at 3:16 on March 3, 2013. The RoCoF during high wind low load condition was less than 0.2 Hz/second and the average time to reach frequency nadir during frequency events is within 4 to 6 seconds. Therefore, the system inertia available in the real time operations under current conditions is still sufficient. However, studies based on 2012 system conditions indicated RoCoF as high as 0.4 Hz/s for two largest unit trip (2750 MW as per recently approved NERC BAL-003 standard). Since there is a declining trend of ERCOT’s inertial response, ERCOT will continue monitoring real time instantaneous penetration of non-synchronous generation and RoCoF during frequency events, and determine when system inertia becomes a reliability concern.

### Synthetic SIR Service

Inverter based wind turbine generators (WTG) and other inverter-based resources can have the capability to inject active power into the system initiated through control system action following a disturbance, e.g. generator trip. This capability, so called synthetic inertia, is already available from several WTG manufacturers. Figure 3 below illustrates synthetic inertial response from a wind power plant with synthetic inertia capability in Hydro Quebec [6]. This capability can be achieved without pre-fault wind energy curtailment. However, when a wind turbine is operating just below rated wind speed there will also be a recovery period shown in Figure 3 below.

Figure 3: Synthetic inertia response from a wind power plant, example of a recorded event in Hydro-Quebec [6] (PCC – Point of Common Coupling, connection point to the grid)

Synthetic inertia capability requires control action in response to falling system frequency and therefore is not equivalent to synchronous machine inertia, which is a natural response of synchronous machines to a generator trip.  However, synthetic inertia will improve RoCoF and help to arrest system frequency decay. More discussion and evaluation of synthetic inertia performance is required.

### Market Construct for SIR

In the near-term, there may be sufficient SIR available naturally to preclude the need for an explicit procurement of this service. Consequently, ERCOT suggests that this service be considered on a different time track and implementation sequence. The goal is to create a market-based process for procuring SIR.  If a reliability need for additional SIR above the naturally-occurring level is seen prior to the time that the market-based procurement process is implemented, a manual implementation as part of the RUC process could be developed first with the market system changes following as soon as practical.

For the initial rollout of procuring the SIR service, ERCOT shall determine the amount of SIR that is required for each hour.  During the initial rollout (transition) period of procuring the SIR service, the required SIR amounts will be acquired through a RUC process if necessary. In this transition period, there will not be a market for this service and no clearing prices for SIR. The RUC optimization engine will seek a resource commitment solution that minimizes resource costs for the Operating Day while simultaneously satisfying the requirements for an amount of SIR service in each Operating Hour based on the physical attributes of the RUC committed resources capable of providing an SIR response.  The resulting RUC unit commitment will represent the least cost commitment and energy dispatch that simultaneously satisfies the SIR constraint.  In the event that the RUC SIR constraint is not satisfied by the final RUC commitment, ERCOT Operations will use a manual processes to satisfy the required system SIR response.

Note that DAM is not considered as the method to procure this service as resource participation in DAM is voluntary and the DAM results are financially binding, not physically binding.  Also from a market pricing process, an inertial response is not provided instead of anything else; therefore, there is no opportunity costs due to this service, no explicit offer into the DAM and the DAM shadow price associated with this service cannot be interpreted as representing an opportunity cost.

The goal is to setup a market procurement process for SIR. Such a market-based process would consider a system requirement for the total amount of H·MVA for each hour of the next day.  Note, MVA is the machines rated capacity in Mega Volt – Amperes  and H is the figure of merit used to analyze the synchronous machine’s inertial response and is referred to as the machine’s inertia constant in seconds.  Offers from generators to provide SIR would be evaluated based on this total requirement and a commitment from the generator to be on-line at the given hour given that generator’s H·MVA. Thus a offer stack can be created with the lowest priced SIR increasing until the total requirement is reached; thus setting the MCP of SIR for the hour.  More discussion will be required to determine the market structure for procuring SIR service. Another option may be to consider the use of an administrative sloped SIR demand curve coupled with SIR offers at an offer price of zero. In the RUC process, the resulting intersection of the SIR supply and demand curve will determine the clearing price of this service.  This clearing price will be paid to all Resources providing this service.  Discussion for creating a market structure for the procurement of SIR needs to include topics such as mitigation of market power, ability to incorporate non-zero SIR Offer prices, etc. [the market structure for procuring SIR service must be set up now if this is something we must have in the future as accommodating it in forward contracts must be managed by all market participants and retail consumers.  If this new service is really required, then we should only have one market disruption with changing to new services not do it twice as this proposes]

### Transition and Implementation Considerations for SIR

Implementation details that require further study include, but are not limited to, the identification of:

- Trending the available SIR in the ERCOT system

- Developing procedure to determine SIR requirements

- Obtaining H and MVA for each generator in ERCOT capable of providing a SIR response,

- Requirements that may be specific to units capable of providing SIR response,

- Validation and Testing requirements for H and MVA for each generator

- RARF data requirements, and

- The need for generic defaults to satisfy the required RUC inputs, and

- ERCOT qualification and performance monitoring systems.

As noted earlier, in the event that the RUC SIR constraint is not satisfied through evaluation of generation commitments to be on-line, ERCOT Operations will use a manual process to satisfy the minimum required SIR.  Incorporating minimum SIR requirements in RUC as well as associated manual process will require some development.  RUC logic for SIR and unit commitment and de-commitment rules will need to be developed to guide ERCOT Operators in the execution of the RUC processes.  The RUC make whole logic will also require revision to address cost recovery issues that are created by unit commitment instructions.[why? What “issues”?]   These updates to the RUC process are a critical milestone in the implementation timeline for this service.

## Fast Frequency Response (FFR) Service

### Need for FFR Service

With less synchronous generation online, there is a need for fast-acting response (full response delivered within 0.5 seconds) to changing frequency. This fast response can supplement the inherent inertial response from synchronous machines, thus helping with the symptoms of low system inertia. It should be pointed out that FFR cannot completely replace system inertia and will only increase time to frequency nadir allowing sufficient time for PFR to deploy. Presently up to 1400 MW of Responsive Reserve Service (RRS) procured from Load Resources (LR) provide the equivalent of Fast Frequency Response Service  as defined below. Furthermore, multi-stage deployments at different frequency thresholds are proposed to provide frequency stabilization resulting in minimizing the amount of FFR capability deployment during frequency disturbances.

### Purpose of FFR Service

Fast Frequency Response (FFR) is MW response faster than the existing Primary Frequency Response Service (PFR) typically referred to as governor response. .  FFR service will, in the event of a sudden power imbalance, decrease the time to reach the frequency nadir and mitigate the RoCoF in the same period.

During periods with low inertia, i.e. periods with low load/high non-synchronous generation, in the absence of FFR much higher capacity of PFR will be needed to ensure that sufficient capability is available to arrest frequency decay in the event of sudden power imbalance.

Fast Frequency Response service is expected to be procured hourly in DAM, and that a Resource with awarded FFR obligation should provide nearly instantaneous increase in active power output from a Resources or nearly instantaneous reduction in demand, following a frequency event that causes frequency to be below the trip threshold . Total time from the when frequency first reach a specified frequency threshold to the time a Resource provides its full capacity obligation should be no more than 30 cycles and sustained until recalled by ERCOT, at most 10 minutes.  The time for a Resource that is providing FFR following a deployment until the Resource is fully able to perform for a subsequent deployment is 90 minutes. A Resource participating in FFR will need to provide ERCOT high resolution sub-second measurement records for qualification and performance evaluation.

In the current AS framework, Load Resources can provide up to 50% of RRS. In this proposed AS framework, FFR and PFR are highly interdependent and the needs can vary based on the system condition. The amount needed for FFR and PFR are described in the section of Primary Frequency Response (PFR) Service.

### Market, Transition and Implementation Considerations Associated with FFR

Market, transition and implementation considerations associated with FFR are discussed below in the PFR section since FFR and PFR have an interdependency.

## Primary Frequency Response (PFR) Service

### Need for PFR Service

ERCOT is a single Balancing Authority Interconnection and is not synchronously connected with any other interconnections, therefore, ERCOT is solely responsible for maintaining frequency to maintain reliability and meet NERC standard requirements. Within ERCOT, all of the frequency response can only come from Resources within the ERCOT Interconnection.  On July 18 2013, FERC issued a Notice of Proposed Rule Making (NOPR) approving the BAL-003 NERC Frequency Response Standard, which sets Frequency Response Obligation (FRO) for each BA. This requirement sets minimum FRO for ERCOT at 286 MW/0.1 Hz [4].

At a minimum, PFR ancillary service should encompass response characteristic designed to meet the following two types of response:

- Arrest the Frequency Decay and control frequency closer to 60 Hz (settling Frequency), shown as rebound period in the Figure 2.

- Resources providing PFR must be able to respond proportionally to frequency deviation.

### Definition of PFR

Primary Frequency Response (PFR) can be defined as the near instantaneous proportional increase or decrease in real power output provided by a Resource in response to system frequency deviations exceeding a specified threshold. This response is in the direction that stabilizes frequency. Primary Frequency Response is attained due to Governor or Governor like action to quickly act relative to the frequency deviation; this response is generally delivered completely within 12 seconds to 14 seconds. The ability of ERCOT Grid to stabilize after a sudden loss of generation or loss of a large Load is dependent on sufficiency of primary frequency response.  Resources providing primary frequency response must be able to provide continuous full proportional response against the frequency deviation. The performance of these Resources will be measured as defined below:

- Full proportional response must be delivered by 16 seconds (B point) from A point (see Figure 2), droop response will be calculated at 16 seconds; and

- Full proportional response must be sustained for an additional 30 seconds after B point, and droop response will be calculated at 46 seconds.

### Governor Setting Requirement for Generation Resources

A Generator Governor with droop setting not to exceed 5% shall be in-service whenever the Generation Resource is providing energy to the ERCOT Transmission Grid.  All the Resources with PFR responsibility shall have the Governor Dead-Band no greater than +/- 0.036 Hz.  Resources without a PFR responsibility may have the Governor Dead-Band set at +/- 0.05 Hz so that these Generators are not required to provide PFR during normal frequency excursions yet remain active during significant disturbances.

### Resource Limit On Carrying PFR

Resources will be allowed to carry PFR reserve up to the capacity that can be deployed by Governor Action for a 1% change in Frequency outside Governor Dead-band (See Figure 4).  The amount of PFR that can be deployed by Governors for a 1% change in frequency outside the Governor Dead-band, will be based on the median of actual performance of each Generation Resource and Controllable Load Resource in the last three measurable events measured at B point and B+30 seconds point.

This methodology would provide incentives for Resources to improve their droop performance to carry more PFR capacity.  Another advantage with a performance based approach is, if Resources perform poorly, they will be limited on how much PFR they can carry; hence more resources will be carrying PFR reserves, which would further improve Grid Reliability. The performance based PFR capacity limit will work as closed loop feedback to improve PFR performance. Besides the PFR capacity limit proposed above ERCOT will limit Resources from providing more than 20% of the Resources HSL on a single Resource to ensure proper distribution of PFR services.

Figure 4: Resources Ability to Carry PFR Capacity as Percent of HSL Based on Droop Performance

### Determination of Amount of FFR and PFR Reserve Needed

The objective of Fast Frequency Response (FFR) and Primary Frequency Response (PFR) Reserves should be to ensure Frequency is arrested above the Under-frequency Load Shedding (UFLS) threshold of 59.30 Hz and to meet NERC FRO Standard (BAL-003). Frequency Response Obligation (FRO) for ERCOT is determined based on simultaneous loss of two largest nuclear units (2750 MW).  In the current AS framework, Load Resources can provide up to 50% of 2800 MW RRS.  The results in the ERCOT 2012 Load Resources assessment further indicated a need of a minimum of 2800 MW total RRS under certain worst case conditions, if that total meets certain minimum Load Resources participation criteria, otherwise additional RRS provided by Generation Resources needs to be procured to provide acceptable response for the outage of two largest units.  In this proposed AS framework, therefore, FFR and PFR are highly interdependent and the needs can vary based on the system condition.  ERCOT should regularly perform the assessment to determine and revise the amount needed for both FFR and PFR.

The previous study by ERCOT, described above, indicates that a minimum of 2800 MW total PFR and FFR Reserve would be required to meet the FRO requirement, if that total meets certain minimum FFR participation criteria, otherwise additional PFR would be required.  Table 2 below illustrates the concept of interdependency between FFR and PFR.

| System Load | FFR | PFR(5% Droop) [please provide the details of these calculations] |
| --- | --- | --- |
| <=35000 MW | 840 MW(30% 0f 2800) | 1960 |
| <=35000 MW | 0 MW | 4480 MW |

Table 2: Requirements for Combined FFR and PFR

### Market Construct for FFR and PFR

The desired system response characteristics to an under-frequency contingency event can be achieved with different amounts of FFR and PFR but the amounts required are interdependent.  Because of this interdependent relationship and substitution capability, ERCOT proposes for consideration by the stakeholders, the treatment of FFR and PFR services as a single market.  ERCOT also proposes that further discussions, as described below, are needed with regard to substitution rules or the separation of the PFR and FFR markets before adopting further changes to the existing market structures for these two services.

ERCOT will determine the total requirement for the sum of FFR and PFR services for each Operating Hour and procure in the DAM an amount of FFR and PFR capacity that satisfies the total requirement.  The QSE’s obligation for these services will be allocated on Load Ratio Share (LRS) basis and self-arrangement is allowed.    QSEs representing Resources that are qualified to provide PFR service may submit offers in the DAM to provide either PFR Service or energy and the DAM optimization engine will award the service based on the co-optimization of the cost of the PFR capacity reservation or energy production, subject to the constraint on the total FFR plus PFR awards.   The SASM process will be utilized to address shortage issues that arise because of AS infeasibility, failures to provide the service, or the need to procure additional PFR and FFR service during the Operating Day.  If the DAM or SASM is unable to satisfy the total FFR plus PFR constraint, ERCOT will use the RUC process to assure that the FFR plus PFR service requirement is met.  Resources awarded PFR service will require a HASL set point that includes the PFR capacity procured by ERCOT.

In addition to the substitution issues discussed above, ERCOT also wants to designate a minimum amount of FFR service when appropriate.  Because of the very short response time upon activation of the FFR service, ERCOT wants to be able to require that a minimum amount of FFR service be online in each operating hour when it is necessary to assure an acceptable system response to the most limiting event applicable for that operating hour. Similarly, there may be conditions under which a minimum amount of PFR service is required. Consequently, ERCOT proposes consideration be given to procuring a minimum amount of each service (FFR and PFR) when needed with the balance of the system needs satisfied solely by the economic optimization between FFR and PFR services, subject to substitution rules.

Another market construct would be to treat PFR and FFR as stand-alone services, such that, FFR offers are cleared to meet FFR requirements and PFR offers are cleared to meet PFR requirements.  ERCOT notes that several market issues could potentially arise with the introduction of PFR and FFR services as stand-alone services. The opportunity costs associated with these services differ depending on the division of the service into a required minimum amount and the balance of the system requirements for FFR and PFR services.  In the case of the minimum procurement amount, the opportunity cost associated with FFR provided by Load Resources is a forward cost incurred by the loss of productivity represented by the disconnected load offset by savings attributed to reduced energy billings.  Other than the submitted offers, ERCOT systems have no way to value these components for inclusion in the DAM constraint model; the constraint model will simply require a minimum procurement amount.  On the other hand, FFR providers will directly compete with PFR provides for the remaining FFR required capacity required to fill out the AS Plan requirements.  FFR offers will be valued according to the DAM co-optimization of PFR reservation capacity and energy.  The difference in pricing between these two capacity regimes will affect the clearing price for the FFR service.  If the clearing price for FFR service is determined by the highest offer struck to achieve the minimum FFR procurement amount, there may be no price incentive for offers beyond this amount.

### Transition and Implementation Considerations Associated With FFR and PFR

The implementation of this service in the ERCOT Operations and Market Operations Systems will require Nodal Protocol changes and extensive process and system upgrades.  These changes will address the following:

- ERCOT Operations AS Plan, AS Qualification and Monitoring processes,

- ERCOT Market Operations DAM and SASM procurement processes (including substitution rules),

- ERCOT RUC process,  ERCOT Settlements and Billing processes, and

- ERCOT qualification and performance monitoring systems.

It is noteworthy, that the efficient use of Generation Resources and the consequent minimization of energy cost would be significantly enhanced by the implementation of a near real time procurement process based on a multi-interval commitment process.   Such a process would provide superior results in the energy, FFR and PFR co-optimization during real and near real time intervals.

For a variety of reasons, including system reliability and security, operation within the NERC standards, and good utility practice, ERCOT also proposes to continue the requirement that all units capable of governor response have their governors in service at all times; however, units that do not have a PFR service responsibility are not required to reserve capacity for governor action and may be allowed to have a larger frequency dead-band as specified above.

## Regulating Reserve Service (Up & Down)

### Need for Regulating Reserve Service (Up & Down)

ERCOT generation is dispatched through Security Constrained Economic Dispatch (SCED) to balance the generation and demand [SCED should only be dispatching to the sum of the generation at the time of the SCED run and neither add or subtract energy from the system.  Doing so causes LFC to have competition and makes it much more difficult to tune.  As such SCED should do nothing to balance generation and demand and all should be controlled solely by LFC].  The power imbalance between each SCED interval will cause frequency deviation that requires regulating reserve to compensate.  Regulation service will not substantially change from where it is today. The proposed changes are discussed in next section.

### Purposed changes for RR Service (Up & Down)

When calculating the amount of Regulation needed, ERCOT should take into account the net load variability, short-term load forecast and the probability of extreme changes such as weather.

Since Regulation is intended to balance the system between five-minute SCED intervals, their deployment and recall capability needs to be consistent. Resources providing Regulation should be limited to min(NURR,NDRR)*5*0.70, where NURR and NDRR are Normal-Up Ramp Rate and Normal-Down Ramp Rate The factor of 0.7 is included to prevent SCED from using up the entire ramping capability on units carrying Regulation, thus leaving 70% ramping capability to respond if Regulating Reserve deployment is needed. .

Resources providing regulating reserve should be able to closely follow ERCOT Load Frequency Control (LFC) signal for Regulation to be effective. Resource specific LFC signals will be delivered by ERCOT to the QSE for providing this service. [ transmission security is a very poor argument for unit specific Regulation as it typically averages zero and there is no mechanism from ERCOT Protocols or its security systems to tell LFC to inhibit such controls] Resource specific deployment will allow ERCOT to implement a pay-for-performance settlement mechanism and assure that each Resource that was awarded Regulation Service in the DAM is indeed providing that service when deployments occur.  [PUC rules require unit specific offers for Ancillary Services and may require same for deployments.] The deployment instructions will be determined by taking into consideration parameters of each individual Resource including Resource specific Raise and Lower blocks as telemetered by the QSE.  The performance measurement should include a metric that correctly measures a Resource’s ability to follow the ERCOT LFC signal and the pay for performance metric should be considered to encourage each Resource to provide the performance required.

Resources providing Regulation service must be able to deliver and sustain the reserve deployments for up to 10 minutes. ERCOT will have to re-visit its LFC and Resource Limit Calculator (RLC) in order to minimize deployments of Regulation for more than 10 continuous minutes in one direction during normal operation. [ not sure this is possible;  the requirement is to provide a specific amount of Regulation for 5 minutes of continuous Reg-up or Reg-Down]  this may not be possible to limit to 10 minutes if you are responding to fast load pick-up or a unit forced outage. Excessive deployments of Regulation can be minimized by re-running of SCED outside its normal periodicity.  In some older systems this was automatically done to prevent overuse of Regulation service. Should SCED run every 3 minutes for example all the time;  maybe it’s time to do that]

]

ERCOT will limit Resources from providing a large amount of Regulation on a single Resource to ensure proper distribution of Regulation services.  [This is now accomplished by the ramp rate on the unit;  what else is needed and why?]

### Market Construct for Regulation (Up & Down)

ERCOT will determine the required amount of Regulation-Up and Regulation-Down capacity for the system for each Operating Hour and procure the needed amount of Regulation capacity in the DAM.  QSEs representing Resources qualified to provide this service may submit offers in the DAM to provide either Regulation Service or energy and the DAM optimization engine will award the service based on the co-optimization of the cost of the Regulation capacity reservation or energy production.  QSE Regulation Obligations will be allocated on LRS and self-arrangement is allowed.  The SASM process will be utilized to address Regulation shortage issues that arise because of AS infeasibility, failures to provide the service, or the need to procure additional Regulation service during the Operating Day.  If the DAM and SASM are unable to award sufficient Regulation service, ERCOT will use the RUC process to assure that the Regulation service requirements are met. Resources awarded Regulation will require a LASL/HASL set point that includes the Regulation capacity procured by ERCOT.

### Transition and Implementation Considerations Associated with Regulation (Up & Down)

The implementation of Regulation in the ERCOT Operations and Market Operations Systems will require Nodal Protocol changes and extensive process and system upgrades.  These changes will address the following:

- The ERCOT and QSE SCADA systems,

- ERCOT Operations AS Plan, AS Qualification and Monitoring processes,

- ERCOT Market Operations DAM and SASM procurement processes (including substitution rules),

- The ERCOT RUC process,

- ERCOT Settlements and Billing processes, and

- ERCOT qualification and performance monitoring systems.

## Contingency Reserve (CR) Service

### Need for CR Service

NERC Standard BAL-002-1 Disturbance Control Standard (DCS) requires ERCOT to carry enough reserve to recover its Area Control Error (ACE) to pre-disturbance level, post DCS event, within 15 minutes.  In order for ERCOT to meet the requirements of the NERC Reliability Standard (BAL-002), ERCOT needs to identify its "Most Severe Single Contingency" to determine their minimum Contingency Reserve requirement.

### Purpose of CR Service

Contingency Reserve is to ensure that Balancing Authority is able to restore Interconnection frequency within defined limits following a DCS event within 15 minutes and restore its Primary Frequency and Regulating Reserve.  Following the frequency restoration, a reserve restoration period of 90 minutes is established in the NERC standard. Contingency Reserve may also be deployed on detection of a large net load forecast error and subsequently restored using Supplemental Reserve Service.

The minimum amount of Contingency Reserve required is equivalent to BA’s Most Severe Single Largest Contingency. In ERCOT’s case this would be 1375 MW.  To ensure ERCOT can meet the DCS standard, the CR must be fully deliverable within 10 minutes so that Frequency can be restored to the pre-disturbance level within 15 minutes.  [this can be managed by a much less expensive service using Supplemental Reserve Service that is available within 30 minutes making the group of market providers larger and potentially much less costly to consumers]

ERCOT Operations will establish a process to identify and flag any need for additional capacity and notify the market through appropriate postings on its web site and if there is insufficient response by the market through the RUC process (same concept as ERCOT Reliability Assessment Tool (ERAT)).

### Qualification of Resources for CR Service

Generating Resources providing CR should be qualified up to the MW value they are able to ramp-up within 10 minutes from the time of deployment. Similarly, Load Resources are qualified for CR based on their ability to decrease energy consumption within 10-minutes from the time of deployment instruction. ERCOT will deploy CR for a sizable generation forced outage. Generation Resources providing CR must telemeter their ramp-rates such that SCED can dispatch the full Resource CR responsibility within 10 minutes. Load Resources providing CR service will be deployed by SCED if its bid price is accepted by SCED.

### Performance Measurement of Resources Providing CR

Generation Resources providing CR should deploy at least 95% of the responsibility within 10 minutes after receiving ERCOT deployment signal. Load Resources providing CR should deploy at least 95% of the responsibility with 10 minutes as measured using a Baseline that is determined by averaging the Resource load over the past 60 minutes.  A resource will be disqualified if it fails two consecutive deployments. [for Load Resources providing CR, it seems as if the load should be measured on its response in RT versus its pattern of use over the prior 60 minutes or so.  Since the need for Frequency Response has been carved out, a load temporarily down and then instructed to not return to service should be allowed to provide CR ]

### Market Construct for CR

ERCOT will determine the minimum required CR for the system for each Operating Hour and procure the needed amount of CR capacity in the DAM.  QSEs representing Generation Resources that are qualified to provide this service may submit offers in the DAM to provide either CR or energy and the DAM optimization engine will award the service based on the co-optimization of the cost of the CR capacity reservation or energy production.    A QSE’s CR obligation will be allocated on Load Ratio Share and self-arrangement is allowed.  The SASM process will be utilized to address CR shortage issues that arise because of AS infeasibility, failures to provide the service, or the need to procure additional CR during the Operating Day.  If the DAM or SASM is unable to award sufficient CR, ERCOT will use the RUC process to assure that the CR requirement is met. Resources awarded CR will require a HASL set point that includes the CR capacity procured by ERCOT.

## Supplemental Reserve (SR) Service

### Need for SR Service

SR service is the reserve that is used to compensate for net load forecast error and/or forecast uncertainty on days in which large amounts of reserve are not available online.  ERCOT is not a part of a NERC Reserve Sharing Group and therefore must maintain sufficient capacity within its boundaries to manage not only system contingencies but also the potential error in its operating Load Forecasts. As such, Supplemental Reserve Service which provides capacity to the Grid within 30 minutes and thus at potentially at a lower cost to consumers may be used to replace Contingency Reserves that may be depleted due to their use to manage a Load Forecast error.

### Purpose of SR Service

ERCOT operations updates its hourly Load Forecast at least once each hour.  These updates and an analysis of the current capacity being provided to ERCOT as reported in each Resource’s COP, the operator can make a reasonable projection if sufficient resources are available to meet the expected demand.  If the operator anticipates that the market will not respond in time, he may deploy Supplemental Reserves to meet those capacity needs.  Supplemental Reserve (SR) Service consists of off-line Generation Resources capable of being started and ramped to a specified output level within thirty (30) minutes or Load Resources that are capable of reducing load demand within thirty (30) minutes and that are capable of running (or being reduced) at a specified output level for at least one (1) hour.  SR may be deployed to replace previously deployed CR, to replace the loss of generating capacity, to cover for insufficient capacity indication in the COP, to compensate for net load forecast error and/or forecast uncertainty.

### Qualification of Resources for SR Service

Generating Resources providing SR should be qualified up to the MW value they are able to ramp-up within 30 minutes from the time of deployment. Similarly, Load Resources should be qualified for SR based on their ability to reduce its energy consumption within 30-minutes from the time of deployment instruction. Load Resources providing SR service will be deployed by SCED if its bid price is accepted  by SCED.

### Performance Measurement of Resources Providing SR

Generation Resources providing SR should deploy at least 95% of the responsibility within 30 minutes after receiving ERCOT deployment signal. Load Resources providing CR should deploy at least 95% of the responsibility with 30 minutes as measured using a Baseline that is determined by averaging the Resource load over the past 60 minutes.

### Market Construct for SR

ERCOT will determine the minimum required SR for the system for each Operating Hour and procure the needed amount of SR capacity in the DAM.  QSEs representing Generation  Resources that are qualified to provide this service may submit offers in the DAM to provide either SR or energy and the DAM optimization engine will award the service based on the co-optimization of the cost of the SR capacity reservation or energy production.    A QSE’s SR obligations will be allocated based on Load Ration Share and self-arrangement is allowed.  The SASM process will be utilized to address SR shortage issues that arise because of AS infeasibility, failures to provide the service, or the need to procure additional SR during the Operating Day.  If the DAM or SASM is unable to award sufficient SR, ERCOT will use the RUC process to assure that the SR requirement is met. Resources awarded SR will require a HASL set point that includes the SR capacity procured by ERCOT.

## Global Market, Transition and Implementation Considerations of New AS

With certain exceptions described below, ERCOT visualizes an AS market procurement process similar to the existing process and continued use of the current market systems.  The new AS products will be incorporated in ERCOT’s daily AS Plan and the required AS services will be procured in the Day Ahead Market similar to today’s Day-Ahead Market.  The SASM process will continue to be used to address changes in AS responsibility due to AS infeasibility, failures to provide the service,  or to satisfy the need for additional AS during the Operating Day. The RUC process will continue to be the backup process for assuring that the requirements of the AS Plan are met.

ERCOT also suggests that consideration be given to implementing SIR, FFR, PFR, Regulation, CR, and SR concurrently with the same commercial operation date.  The initial requirements for SIR may be zero, however the systems build and test will include this service with the expectation that it will be required depending on future resource additions in ERCOT. The Synchronous Inertial Response service may be required to meet system stability requirements before it is possible to complete the system changes required for these three services.

In addition to addressing the PFR/FFR substitution issue, ERCOT proposes that the discussions of the new AS include the concept of price ranking and substitution among the appropriate AS.  Enforcing relative price rules for MCPCFFR/PFR greater than the MCPCRegulation greater than the MCPCCR demonstrates the relative value of each service in the ERCOT system and will help quantify pricing rules when the capacity reserves for each service are compromised by system-wide events.  Such rules can be enforced by use of submission criteria and validation or within the DAM optimization.  Further study and review are needed to ascertain the cost and benefit of the concept and the methodology utilized to enforce relative value constraints.

The necessity of a separate FFR Down and PFR Down service will require further discussions.

ERCOT recommends sufficient notice time of the implementation date of the new AS product set so that the market participants can make/adjust their forward contracts.

ERCOT recommends that, following topics from the workshop on October 24, 2013, be addressed through the stakeholder process:

- Market construct for the procurement of SIR

- Combined procurement of PFR and FFR or procurement of PFR and FFR as stand-alone services

- Consideration of a separate FFR Down Service

- Consideration of a separate PFR Down Service

- Settlements

  - Pay for Performance

  - How AS obligations are determined

- Role of DC ties in providing AS

- Supplemental Reserves should be developed just as any other AS and not be considered a “transition” AS.  SR is less expensive than CR and ERCOT must prove it must have the more expensive service rather than manage with two at less cost to consumers.

- Real-Time Market with energy and AS co-optimization

- Consider running the SCED at a faster periodicity

- ORDC for DAM ( and Real-Time Market)

- Deliverability of AS (AS deliverability zones)

- Changes to Regulation deployment by LFC from portfolio to Resource specific

- How and on what timeline will the PUC chapter 25 rules be modified to account for the new ancillary services suggested here

- market procurement process for SIR must be developed at the same time as the other new AS.

- Review how regulation providers must “sustain the reserve deployments for up to 10 minutes”.

- Review process for obtaining additional AS when DAM is short.  Why not notify market, Run SASM before forcing units with RUC?

- Discuss replacing deployed CR with Supplementatl Reserves as Supplemental Reserves should be less expensive than purchasing more CR than needed to cover forced outages.

- Supplemental Reserve (SR) Service consists of off-line Generation Resources capable of being started and ramped to a specified output level within thirty (30) minutes

- Implement SIR, FFR, PFR, Regulation, CR, and SR concurrently with the same commercial operation date and manage the need for each service via the AS Plan

## Summary of the Proposed Ancillary Services

| Name | Synchronous Inertial Response (SIR) Service |
| --- | --- |
| Purpose | Maintain minimum rate of change of frequency (RoCoF) Provide sufficient time for primary frequency response |
| Background | New technology Base loaded units with smaller inertial response have replaced many of the older Boiler/turbine/generators when the current set of Ancillary Services were developed to manage reliability High non-synchronous generation penetration can de-commit synchronous generators Peaking units with smaller inertia can replace base units to support system variations Low inertia will result in quicker frequency decay and lower frequency nadir during generator outage |
| Qualification | Resource with synchronous rotating mass Resource with simulated fast response through use of electronic systems(Synthetic SIR Service) |
| Resource Limit | Quantity for the Resource’s inertia contribution is determined as: H ·MVA where H is machine inertia constant in seconds, MVA is the machine’s rated output capacity in mega-volt amperes The product H times MVA is the kinetic energy that can be provided by the synchronous machine during system imbalance |
| System Criteria | Maintain appropriate RoCoF Maintain minimum duration from point A to point C, Figure 2 No triggering of UFLS with two simultaneous largest units forced outages |
| Deployment | Instantaneous and continuous self-deployment |
| Performance | Inertial support is a natural characteristic of the synchronous machine and is independent of external control or pre-disturbance power production/consumption. Synthetic SIR Service must meet the same characteristics of a true synchronous machine |
| Quantity | To be determined (study required) This will only be procured for hours when there is a residual need |
| Market Service | Potential need in the future. |
| Comments | Monitor and project the trend of ERCOT system inertial response and RoCoF Identify the minimum needs of system inertia and duration between points A and C, Figure 2, or the maximum possible penetration of non-synchronous generation in ERCOT Conduct a survey and identify the generator’s RoCoF tolerance capability in ERCOT Identify if the need for SIR is locational or system-wide. Investigate value of synthetic inertia from wind farms for system’s SIR Investigate potential means of validation of service provision |

| Name | Fast Frequency Response (FFR) Service |
| --- | --- |
| Purpose | Supplement to inertial response Improve RoCoF after FFR deployment Improve frequency nadir Provide sufficient time for primary frequency response |
| Background | New technology Base loaded units with smaller inertial response have replaced many of the older Boiler/turbine/generators when the current set of Ancillary Services were developed to manage reliability High non-synchronous generation penetration can de-commit synchronous generators Peaking units with smaller inertia can replace base units to support system variation Low inertia will result in quicker frequency decay and lower frequency nadir during generator outage |
| Qualification | Resources need to inject full responsibility within 30 cycles, and maintain production output for at least 10 minutes Resources need to provide high resolution data. |
| Resource Limit | The capacity that a resource can respond within 30 cycles and sustain for at least 10 minutes. |
| System Criteria | Maintain a minimum of RoCoF Maintain minimum duration from point A-C No triggering of UFLS with two simultaneous largest units forced outages |
| Deployment | Self-deployment though automatic controller or relay Staged based on the defined trigger threshold that can be multi-stage deployment. |
| Performance | Fully self-deployed within 30 cycles at specified frequency threshold Production output sustained for at most 10 minutes or recalled by ERCOT signal |
| Metric | Resource needs to provide the deployment records to ERCOT Resource needs to deploy a minimum of 95% or maximum of 110% of the awarded obligation within 30 cycles and sustained for at least 10 minutes. Need to pass above 90% of the previous months’ deployment or cannot have two consecutive failure performance if less than one deployment in a month. |
| Quantity | A minimum of xx MW Highly interdependent with the amount available for PFR |
| Market | FFR needs to be implemented with PFR together |
| Comments | Multi-stage deployment Time for a Resource that is providing FFR following a deployment until the Resource is fully able to perform for a subsequent deployment maximum restoration time for deployed FFR amount is 90 minutes Identify the minimum and maximum quantity for this service. Currently, up to 1400 MW LRs in the RRS to provide FFR-like support. Identify the relation between FFR and PFR. For example, if PFR is under procured, what is the additional need from FFR and vice versa? Technology-neutral requirements might be a challenge for this service. Frequency thresholds can be resource (or technology) specific. For example, LRs at 59.7 Hz and storage at 59.91 Hz in order to better utilize the resources’ capability. Investigate if ERCOT needs FFR DOWN Reserve in future or not Investigate if a Load Resource that is currently providing RRS also provide FFR and CR just on differing time scales Investigate potential means of validation of service provision |

| Name | Primary Frequency Response (PFR) Service |
| --- | --- |
| Purpose | Arrest frequency decay and restore frequency to near 60Hz Improve frequency nadir Meet NERC BAL-003 (FRO) |
| Background | ERCOT is required to meet NERC BAL-003 to avoid triggering UFLS with losing two largest units. The first stage for UFLS is currently set at 59.3 Hz. |
| Qualification | Biennial Governor Tests |
| Resource Limit | Capacity that can be deployed by Resources Governor’s for 1% change in Frequency outside Governor Dead-band How much PFR can be deployed by Governors for 1% change in Frequency outside the Governor Dead-band, will be based on median of actual performance of the Generation Resources and Controllable Load Resources in last three measurable events measured at B point and B+30 seconds point |
| System Criteria | No triggering of UFLS with two simultaneous largest units forced outages Procure Resources directly |
| Deployment | Automatic Self-deployment with proportional response |
| Performance/Metric | Performance measured during Measurable Events at B point and B+30 point to calculate droop performance Sustained continuously against frequency deviation |
| Quantity | Depends on how much FFR is procured |
| Market | Yes, PFR needs to be implemented with FFR together |
| Comments | A Governor with droop setting not to exceed 5% shall be in-service whenever the Generation Resource is providing energy to the ERCOT Transmission Grid. All the Resources with PFR Obligation shall have the Governor Dead-Band no greater than +/- 0.036 Hz. As a concept, a Resource without a PFR Obligation may have the Governor Dead-Band set at +/- 0.05 Hz. so that these Generators are not required to provide PFR during normal frequency excursions. Investigate pay for performance metric. Review need for special telemetry to obtain fast response data of providers to verify performance |

| Name | Regulating Reserve (Regulation) Service |
| --- | --- |
| Purpose | Match generation and demand between SCED interval To restore the PFR reserve Meet NERC BAL-001 (CPS1) |
| Background | Regulation is needed to correct short-term power imbalance between each SCED interval There is Regulation-Up and Regulation-Down |
| Qualification | QSEs are capable to receiving Regulation control information on a unit specific basis and sending ERCOT recommended control actions to the individual Resource Resources can continuously receive and follow ERCOT Load Frequency Control (LFC) signal |
| Resource Limit | min(NURR, NDRR)*5*0.7, where NURR and NDRR are Normal-Up Ramp Rate and Normal-Down Ramp Rate |
| System Criteria | Procure enough capacity to correct net-load variations [load forecast error should not be part of reasons to use Regulation. It does not matter what the forecast is as LFC is always controlling against ACE; SCED should run based on sum of Generation that that takes into account any load forecast error.] Procure Resources directly |
| Deployment | Following ERCOT LFC signal |
| Performance | Recommend new performance metric for each Resource that grades resources based on their ability to closely follow ERCOT LFC signal (similar to PJM). Resources providing Regulation service must be able to deliver and sustain the reserve deployments for up to 10 minutes[see prior comments]. |
| Metric | To be designed around performance requirement |
| Quantity | net load variability, short-term load forecast error; [this should not be in LFC] probability of extreme changes such as weather as applicable |
| Market | Yes, for both UP and DOWN |
| Comments | Deployments to Resources directly [there is no mechanism from ERCOT security systems to tell LFC to inhibit such controls. Any why would you as all regulation is movement of generation is temporary anyway and not sustained] To maximize the benefits of Resources with different characteristics, ERCOT will use customized LFC control for each Resource Investigate different performance metric that measures resources response accurately and explore the concept of pay for performance |

| Name | Contingency Reserve (CR) Service |
| --- | --- |
| Purpose | To cover the Most Severe Single Contingency (MSSC) To restore other AS reserve [use of CR is not to restore reserves of other AS but to release more reserves to SCED; Supplemental Reserves can be used to restore CR] |
| Background | CR is need to restore the frequency back to pre-disturbance level within 10 minutes [ these reserves must be “restored” by re-running SCED immediately to account for the change in generation that took place when PFR and Regulation Reserve was used] |
| Qualification | Resources should be qualified based on their ability to ramp within 10 minutes [ should this not be better specified as the Resource’s minimum emergency ramp rate times 10 over the full range of operation of the unit between HSL and LSL] |
| Resource Limit | Up to the HSL demonstrated during HSL testing Resource’s minimum emergency ramp rate times 10 over the full range of operation of the unit between HSL and LSL |
| System Criteria | To cover the loss of up to the MSSC per NERC BAL-002 To restore PFR and Regulating Reserves Deployment of these reserves should not violate security constraints. |
| Deployment | SCED, using Offer curves for Generation Resources and Bid curves for Load Resources |
| Performance | Resources providing CR must telemeter ramp-rates such that SCED can dispatch the full CRS capacity that the Resource is obligated within 10 minutes. Generation Resources must reach 95% of the SCED BP within 10 minutes. Load Resources providing CR should deploy at least 95% of the responsibility within 10 minutes as measured using a Baseline that is determined by averaging the Resource load over the past 60 minutes. |
| Metric | Resources providing CR must telemeter as a minimum the ramp-rate such that SCED can dispatch the full CR capacity that the Resource is obligated within 10 minutes. Generation Resources must reach 95% of the SCED BP within 10 minutes. Load Resources providing CR should deploy at least 95% of the responsibility within 10 minutes as measured using a Baseline that is determined by averaging the Resource load over the past 60 minutes. Failure to meet any requirement stated would result in disqualification from providing CR. Once disqualified, the Resources can request for requalification any time after 30 days Resources providing CR must be able to deliver and sustain the reserve deployments for the full hour it is carrying that obligation. |
| Quantity | Minimum of at least the MSSC |
| Market | Yes |
| Comments | QSGRS and Load Resources are expected to be eligible to provide this service Deployment of these reserves should not violate security constraints. ERCOT Operations will establish a process to identify and flag any need for additional capacity through RUC process (same concept as ERAT) |

| Name | Supplemental Reserve (SR) Service |
| --- | --- |
| Purpose | To cover the loss of generating capacity Compensate for net load forecast error and/or forecast uncertainty To restore other CR reserve following a deployment |
| Background | SR is need to restore the CR, FFR,PFR and Regulation |
| Qualification | Generation Resources must be off-line to provide SR. Generation Resources should be qualified based on their ability to ramp within 30 minutes Load Resources should be qualified for SR based on their ability to reduce its energy consumption within 30-minutes from the time of deployment instruction. |
| Resource Limit | Up to the level demonstrated during qualification testing |
| Deployment | Generation Resources are committed by SCED based on start-up prices and energy offers for the expected run time of the need for the Resource Load Resources providing SR service will be deployed by SCED if its bid price is accepted by SCED |
| Performance | Off-Line Generation Resources providing SR must start and reach the full SR capacity that the Resource is obligated within 30 minutes. Load Resources providing CR should deploy at least 95% of the responsibility with 30 minutes as measured using a Baseline that is determined by averaging the Resource load over the past 60 minutes. . |
| Metric | Resources providing SR must telemeter ramp-rates such that SCED can dispatch the full CR capacity that the Resource is obligated within 30 minutes. |
| Quantity | Determined based on load forecast uncertainty |
| Market | Yes |

# References

- System Inertial Frequency Response Estimation and Impact of Renewable Resources in ERCOT Interconnection; Sandip Sharma, Shun-Hsien Huang and NDR Sarma

- ERCOT System Planning Report for ROS, July 2013. Available at: http://www.ercot.com/calendar/2013/08/20130815-ROS

- Reliability Guideline: Reserve Policy; NERC

- NERC BAL-003 Standard

- DS3: System Services Review TSO Recommendations, EirGrid (System Operator of Republic of Ireland), SEMO (Single Electricity Market Operator of the Republic of Ireland and Northern Ireland), SONI (System Operator of Northern Ireland)

- Wind Power Status and Experience with Inertial Response from Wind Power Plants; Noel Aubut, Hydro-Quebec TransEnergie, presentation from 2nd Workshop on Active Power Control from Wind Power, Boulder, Co, May 2013

# Footnotes

The ACE is an error signal generated in the ERCOT Load Frequency Control system that determines the direction and magnitude of the regulation control signals provided to those resources providing Regulation Up or Down AS.

Available at http://www.ercot.com/calendar/2012/06/20120614-ROS

ERAT is a tool developed at ERCOT to assess operational, e.g. day ahead or hour ahead, loss of load probability LOLP.