## Slide 1: PGRR031
ROS – November 14, 2013

## Slide 2: Background
May 2011: ERCOT BOD directs TAC to report on recommendations for addressing gaps between operations and planning
Feb 2012: ROS forms OPSTF to address gaps between operations and planning with a list of issues to address
April 2013: OPSTF recommends that PLWG revise the planning criteria to 95% loading limit; ROS endorses recommendation
Addresses four issues from OPSTF issue list
June 2013: PGRR031 posted
Issue/ PGRR discussed at May, June, August, September, and October 2013 PLWG meetings

## Slide 3: OPSTF issues addressed by PGRR031
#3: Ensuring projects in the Five Year Transmission Plan are completed in a timely manner. This includes unforeseen consideration of load variability, transmission outages and construction complexities that may require earlier completion.
#4a: Appropriate Ratings - Ensure Load and Ratings assumption consistency.
#4c: Appropriate Ratings - Should planning studies be more conservative by using the planning normal rating (Rate A) for a select set of contingencies?
#8c: Generator unit unavailability and modeling issues - Use of “typical” or “historical” Planned, Maintenance and Forced Outages and/or derates in an area

## Slide 4: OPSTF observations
Construction delays for projects planned to resolve a constraint could lead to overloads in real-time until the planned project is complete. This could occur for multiple summer seasons depending on the length of the delay.
The current practice to test the unavailability of any given unit in planning studies may miss overloads that occur in operations when multiple units in an area are out of service or derated. Historically over summer peak as much as 10% of capacity in ERCOT has been either derated or unavailable altogether. OPSTF analysis shows that this could increase loadings on circuits by 4% or higher.
During severe weather that results in higher than anticipated temperatures and higher associated load conditions, facility thermal ratings are generally lowered for studies run by transmission operators per their ambient temperature adjusted dynamic ratings. As an example, one large TSP noted that if the temperature were just 4 degrees F higher than the assumed static rating temperature (104 degrees F) the dynamically rated lines on their system would be rated 3% below the static rating. Since planning reliability studies use static ratings, overloads may be observed in operations under these conditions.
Planning analysis utilizes load forecasts made several years before the operating conditions are realized. Sometimes load grows faster than anticipated and overloads occur in operations because the load level was not seen soon enough in the planning analysis to get the necessary improvements constructed. For example, the recently completed 2012 Five-Year Transmission Plan identified 20 reliability problems for summer 2013 for which the transmission solution for those problems will not be constructed before the problems will occur.
Planning analysis assumes that all facilities are in-service. However, even over summer peak there is equipment that is out of service for maintenance, construction, or for an extended forced outage. This leads to line loadings in operations that are higher than anticipated in planning studies.
Actual generation dispatch is different from that modeled in planning cases.
Construction and maintenance clearances are not known when planning studies are performed. During real-time operations, multiple clearances are in effect which cause SCED and RTCA results that differ from planning studies.

## Slide 5: 4.1.1.2 Language addition highlight
(2) The minimum performance criteria requires loading on Transmission Facilities to remain less than or equal to 100% of their applicable Ratings. However, for Transmission Facilities with loading greater than or equal to 95% of their applicable Ratings under normal system conditions and under contingency events identified in paragraph (1)(a) and Line 1 of Table 1 above, TSPs and ERCOT shall initiate and pursue projects to be in service in a timeframe consistent with loading greater than or equal to 95%. ERCOT shall endorse projects as applicable.
  (a) For normal system conditions and the conditions described in paragraph (1)(a) and Line 1 of Table 1 above, TSPs and ERCOT may elect not to initiate and pursue projects for Facilities loaded between 95% and 100% of their applicable Ratings if the loading on those Transmission Facilities is not expected to significantly change within the six-year planning horizon. Examples of such Transmission Facilities may include, but are not limited to, transmission circuits that are radial to Generation Resources where the maximum output of the Generation Resources is not expected to increase within the six-year planning horizon and transmission circuits that are radial to Load that is not expected to significantly increase within the six-year planning horizon.

## Slide 6: PGRR031 FAQs
Q: Will the proposed PGRR031 create many new transmission projects?
A: ERCOT conducted an analysis of the impact of the 95% criteria using the 2012 5YTP and presented it to the OPSTF. The analysis identified 40 elements loaded between 95% and 100% in the 2015 case. The TSPs indicated that most of the circuits were already being addressed by projects scheduled to come in-service a year or two later.
Q: What is the impact of the proposed PGRR031 on facilities from generators or in areas where the load is not growing?
A: 4.1.1.2 (2)(a) contains an exemption for facilities where the loading is not increasing in the planning horizon.

## Slide 7: PGRR031 FAQs
Q: What is the 95% loading recommendation based upon?
A: No – OPSTF considered 90%, 95%, and 97% but settled on 95% for the recommendation based on careful analysis of equipment derates at higher temperatures, circuit loading increases for multiple generator outages in an area, and line loading increases year over year.
Q: What are other recent OPSTF and PLWG changes to the planning criteria?
A: Only one other PGRR (PGRR025, Addition of Criteria for Autotransformer Unavailability) has resulted in planning criteria changes based on OPSTF recommendations in response to the ERCOT BOD directive. [PGRR026, Addition of Year 6 to the SSWG Base Cases, also addressed an OPSTF issue, but was primarily driven by NERC requirements and the increasing lead time necessary to construct new transmission lines in Texas.]

## Slide 8: PGRR031 FAQs
Q: If a line is loaded at 95% in the year 6 case, what will be done?
A: First, a project will be identified to resolve the loading (assuming it doesn’t meet the 4.1.1.2 (2)(a) exemption criteria). If the identified project does not require immediate action in order to have it in service by year 6, the project will be reevaluated in subsequent assessments. If the project requires action now in order to have it in service by year 6, ERCOT and the TSP(s) will pursue the project in order to have it in service by year 6.
Q: When will this criteria change be implemented?
A: 4.1.1.2 (3)(b) allows for a 36 month implementation period.

## Slide 9: PLWG Discussion
Most PLWG attendees supported the PGRR
  General agreement with OPSTF observations
A few PLWG attendees did not support the PGRR
  Concern expressed that the PGRR will lead to unneeded transmission projects getting constructed
  Transmission vs. generation

## Slide 10: Questions?