2705 West Lake Drive

Taylor, Texas 76574

# Ratings Usage Whitepaper

Version 1.0

John Moseley

7/30/2010

Revision History

| Revision | Comments | Date | Author |
| --- | --- | --- | --- |
| 1.0 | Initial Version | 7/30/2010 | John Moseley |

Background

Due to the design of downstream systems, the following are two sets of ratings structures that the NMMS must currently support.

- Measurements  for storing Ratings

  - Hierarchy

    - Equipment {TransformerWindings, ACLineSegments, SeriesCompensator}

      - Terminal (near = True)

        - Analog (forNetwork= T , PositiveFlowIn = T)

          - AnalogLimitSet

            - AnalogLimit (LimitType = Normal)

            - AnalogLimit (LimitType = TwoHr)

            - AnalogLimit (LimitType = FifteenMinute)

        - Analog (forNetwork= T , PositiveFlowIn = F)

          - AnalogLimitSet

            - AnalogLimit (LimitType = Normal)

            - AnalogLimit (LimitType = TwoHr)

            - AnalogLimit (LimitType = FifteenMinute)

      - Terminal (near = False)

        - Analog (forNetwork= T , PositiveFlowIn = T)

          - AnalogLimitSet

            - AnalogLimit (LimitType = Normal)

            - AnalogLimit (LimitType = TwoHr)

            - AnalogLimit (LimitType = FifteenMinute)

        - Analog (forNetwork= T , PositiveFlowIn = F)

          - AnalogLimitSets

            - AnalogLimit (LimitType = Normal)

            - AnalogLimit (LimitType = TwoHr)

            - AnalogLimit (LimitType = FifteenMinute)

  - Model Requirements

    - Atleast one among  a.a and a.b must be defined at Terminal (near = True)

    - Atleast one among  a.a and a.b must be defined at Terminal (near = False)

  - Consumption(Downstream system that reads this data)

    - MMS

      - Utilizes a conservative approach and stores Minimum value for each limit type (Normal, TwoHour, FifteenMinute). i.e.

Normal_Limit = MIN(1.1, 1.1, 2.1, 2.1)

TwoHr_Limit = MIN(1.2, 1.2, 2.2, 2.2)

FifteenMin_Limit = MIN(1.3, 1.3, 2.3, 2.3)

      - These limits are used as default static limits of the equipment for powerflow studies. (Default i.e. no limit is transferred from EMS to MMS).

    - EMS

      - Stored in Netmom with the expectation that all values for the same limit type will be the same i.e.

Normal_Limit = 1.1 = 1.1 = 2.1 = 2.1

TwoHr_Limit = 1.2 = 1.2 = 2.2 = 2.2

FifteenMin_Limit = 1.3 = 1.3 = 2.3 = 2.3

      - Used as equipment limits when power flow-like studies are run in an environment devoid of realtime telemetery and dynamic limits-override (STNET-type environments) .

- OwnerShareRatings for storing Ratings

  - Hierarchy

    - Equipment  {TransformerWindings, ACLineSegments, SeriesCompensator}

      - OwnerShareRating (RatedBy = TDSP)

        - Rating (RatingType = Static)

          - AnalogLimit (LimitType = Normal)

          - AnalogLimit (LimitType = TwoHr)

          - AnalogLimit (LimitType = FifteenMinute)

          - AnalogLimit (LimitType = Conductor)

        - Rating (RatingType = Dynamic, activateValue = [20, 25,…, 115,120])

          - AnalogLimit (LimitType = Normal)

          - AnalogLimit (LimitType = TwoHr)

          - AnalogLimit (LimitType = FifteenMinute)

  - Model Requirements

    - A single StaticRating (a.a) must always be defined for an equipment.

    - 20 temperature-based DynamicRatings must be present when the equipment is dynamically rated.

    - Mutliple sets of OwnerShareRatings (1) may be defined when a dynamically rated equipment is jointly rated.

  - Consumption(Downstream system that reads this data)

    - Planning

      - Equipment/Branch limits.

      - ConductorRating is considered as the third limit.

    - EMS

      - For each dynamically rated equipment, all ratings defined under 1  are stored on a per owner basis.

      - Effective equipment limit is derived from this set for an effective Temperature definition and utilized in power flow studies (RTNET and STNET type environment can use these).