## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: November Meeting
Met Nov 19, 2013
  25 members representing 15 companies as well as ERCOT & TRE.
NPRR 524 discussion
Release of Reserves under ORDC
Event review
Frequency Control Report Nov 2013

## Slide 3: NPRR 524 Q&A
Q1 - Does the group agree that it was your intent for QSEs to lower the actual HSL in order to comply with NPRR 524?
A1- The intent was for QSEs to lower the HSL, as is currently required, to comply with NPRR524. However NPRR524 allows for less stranded MW when carrying Responsive Reserve on a Combined Cycle Facility with Power Augmentation. If the generator can fire the Power Augmentation and reserve frequency responsive capacity then the HSL can include the Power Augmentation Energy.
Q2 - Maybe you should explore a HASL offset. This real time telemetered offset would be added to the Ancillary Service Schedule. That way the HSL is actually the HSL and the HASL offset would push the HASL to the desired level.
A2 - This proposal was discussed and will require a system change. NPRR 429 proposed a similar solution, but still strands the capacity.
Q3 - That leaves you with issue 3 above (withholding). Perhaps the ISO could remove the HASL offset based upon some criteria, but the RRS would no longer meet the primary frequency response obligation.
A3 - No solution is apparent under the current protocols.

## Slide 4: Release of Reserves under ORDC
Assumption: PRC is below 3200MW and 500MW is released to SCED.
Question: How do you release 500MW RRS while maintaining the same level of frequency responsive capacity of the grid?
Issues: Price reversal, timing of reserve deployment (release of capacity), UFR RRS isn’t the same as Generator RRS, {problem with throwing NONPFR resources into RRS pool. Can’t get them out}
Possible solution: remove the 500MW from RRS and put it back in NSRS.
Action: Create possible scenarios and present to ROS

## Slide 5: Event Review
PDCWG Reviewed 1 event
  Good system frequency performance with few poor performers identified
  Non Frequency responsive RRS providers were noted and ERCOT will follow up with QSEs regarding their performance

## Slide 6: Focus for 2013
Formal & documented review/report of frequency responsiveness for Power Augmentation on Combined Cycle Resources (train not individual unit)
Review regulation/GTBD deployment effectiveness (SCR 773)
  Study the impact of HSL/basepoint/generation deviation on compliance and reliability
  Develop metrics to track regulation deployment effectiveness
Pilot of fast frequency response – characterize & create evaluation process
Impact of ORDC market Design
Ancillary Service Overhaul
  No performance required for nonpayment (freq. resp AS)
Fast Responding Regulation – NPRR581 (new)
Responsive Reserve requirements, qualification vs. compliance. (10min vs. 16 second)
Standardized/consistent metrics for PFR analysis (BAL001-TRE).
  Work on realistic measurement of combined cycles
Standardized/reasonable expectations for extreme events (2750MW or larger lost) – driven by NERC.
ERS impact review with appropriate ERCOT group. Target Q1-2014
PMU data understanding of implications
Red = Work on going
Check = completed goal

## Slide 7: ERCOT Frequency Control Report November 2013
Sydney Niemeyer NRG Energy
December 4, 2013

## Slide 8: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.

## Slide 9: Ercot frequency control
BAL-001 CPS 1 & 2 Performance, RMS 1 and Frequency Profile

## Slide 12
CPS1 12 Month Rolling Average = 166.31

## Slide 17
60.015 <= HZ < 60.020

## Slide 19: ERCOT Time error and time correction
Time Error History

## Slide 20: Time Error Corrections
Fifth consecutive month with no manual Time Error Correction.
Prior to July 2013 there have been 3 months with no manual Time Error Corrections. This is between Sept 2001 and June 2013, almost 12 years.
  One in 2004, 2009 and 2011.

## Slide 23
Time Correction History

## Slide 26: Ercot primary frequency response performance
BAL-003-1 Interconnection Frequency Response and Bias Measure.

## Slide 27
ERCOT Primary Frequency Response – BAL-003-1
2014 Bias and Frequency Response Measure Page 1

## Slide 28
ERCOT Primary Frequency Response – BAL-003-1
2014 Bias and Frequency Response Measure – Page 2

## Slide 29: Ercot total energy and wind production
October Total ERCOT Energy and Total Energy Production from Wind Resources.

## Slide 33
Questions?