## 1) General Information
CenterPoint Energy Distribution Loss Factor for 2014
----> | Changes for 2014 are shown in bold red font
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated on December 1, 2010. See following
protocol link: http://www.ercot.com/mktrules/nprotocols/current
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load (15 minute basis)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
----> | AAL value for use in 2014 = 9,290 MWH
AAL value for use in 2013 = 9,304 MWH
AAL value for use in 2012 = 9,463 MWH
AAL value for use in 2011 = 9,034 MWH
AAL value for use in 2010 = 8,785 MWH
AAL value for use in 2009 = 9,043 MWH
AAL value used in 2008 = 8,794 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = 0.016870
F2 = 0.000395
F3 = 0.019770
AAL for ERCOT (15 mins) = 9,290
For "E" Primary Customers
F1 = 0.011192
F2 = 0.000010
F3 = 0.001210
AAL for ERCOT (15 mins) = 9,290
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
Ratio of Peak to AAL
|  | CNP | ERCOT
|  | 2.0211 | 1.8209
Ratio of Peak to AAL for CNP is not proportional to ERCOT
| 2011 for use in 2012 |  | 2012 for use in 2013 |  | 2013 for use in 2014 |  | 2012/2011 | 2013/2012
| 15 mins | 1 hour | 15 mins | 1 hour | 15 mins | 1 hour
CNP Peak | 3777.5 | 15110 | 3690.75 | 14763 | 3687 | 14748 | 0.97704 | 0.99898
CNP AAL | 1859.25 | 7437 | 1817.75 | 7271 | 1824.25 | 7297 | 0.97768 | 1.0036
ERCOT Peak | 17104 | 68416 | 16701.5 | 66806 | 16915.75 | 67663 | 0.97647 | 1.0128
ERCOT AAL | 9463 | 37852 | 9304 | 37216 | 9290 | 37160 | 0.9832 | 0.9985
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2013 for use in 2014 as follows:
1. Substation Transformer Losses (The A B constants for substation transformers were updated for 2014)
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
The total no-load losses are 19.473 MW.
Also, the database provided the total "Load" losses for the transformers on the system at rated trf load.
This value is 51.403 MW at 16,216 MW load level.
This results in a total of 70.876 MW of substation transformer losses at approximately 16,216 MW at CNP.
The constants in the system loss equations were adjusted to match this result. See Tab 3.
2. Primary Conductor Losses (No change in the A B constants for primary conductor for 2014)
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
For 2014, there is no further change in the system loss equations.
3. Distribution Transformer Losses (The A B constants for distribution transformers were updated for 2014)
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the GIS spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for "no-load" losses for a distribution system that has both old and new transformers.
The "load losses" from both methods were very close, so the load losses from GIS were used.
See Tab 3 for the updated A B constants for distribution transformers.
4. Secondary Conductor Losses (No change in the A B constants for secondary conductor for 2013)
The constant in the system loss equation for secondary losses for 2014 is same as used in previous years.
5. AAL for ERCOT
The AAL for ERCOT was updated based on information from ERCOT. The new value for 2014 is 9,290 MWH for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis.
The F1, F2, and F3 coefficients for D secondary customers and E primary metered customers for 2014 are shown above.
Overall results:
For "E" Primary Customers |  |  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 for use in 2014
|  | DLF at AAL | 1.267% | 1.254% | 1.254% | 1.311% | 1.291% | 1.241%
|  | DLF at ERCOT Peak | 2.018% | 2.039% | 2.039% | 2.131% | 2.072% | 2.105%
For "D" Secondary Customers |  |  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 for use in 2014
|  | DLF at AAL | 3.535% | 3.681% | 3.681% | 3.663% | 3.705% | 3.704%
|  | DLF at ERCOT Peak | 4.034% | 4.124% | 4.124% | 4.218% | 4.178% | 4.197%
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-945-4162
or email at richard.moffatt@centerpointenergy.com.
CenterPoint Energy Distribution Loss Factor For 2014
Sept 17, 2013

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis
|  | CenterPoint Energy Distribution Loss Factor for 2014.xls | [13 empty] | With Scaling | Using F1, F2 & F3 Coefficients |  |  | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  | 2013 | Secondary | 2013 | 2013 | 2013 | 2013 | 2013 | Total | 2013 | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 19.4735 | 30.5265 | 0.0010618 | 19.4746 | 38.95% | 30.5254 | 137.7514 | -107.226 | 0.0040754 | 157.2301 | 314.5% | 314.5%
|  |  |  | 135 | 19.4766 | 115.5234 | 0.015206 | 19.4918 | 14.44% | 115.5082 | 137.7573 | -22.2491 | 0.00017547 | 157.2493 | 116.5% | 116.5%
|  |  |  | 500 | 19.5219 | 480.4781 | 0.26304 | 19.7849 | 3.957% | 480.2151 | 137.8603 | 342.3548 | 0.041545 | 157.6867 | 31.54% | 31.54%
1273.1259 | 5092.5038 |  | 250 | 1000 | 19.6685 | 980.3315 | 1.095 | 20.7635 | 2.076% | 979.2365 | 138.2054 | 841.0311 | 0.25072 | 159.2196 | 15.92% | 15.92%
3055.5023 | 12222.009 | 1 | 600 | 2400 | 20.599 | 2379.401 | 6.4507 | 27.0497 | 1.127% | 2372.9503 | 140.4195 | 2232.5308 | 1.7667 | 169.2359 | 7.051% | 7.051% | 6.605% | 0.737% | 1.127% | 1.127% |  |  | 27.0497 | 169.2359
3564.7526 | 14259.0106 | 2 | 700 | 2800 | 21.0056 | 2778.9944 | 8.7993 | 29.8049 | 1.064% | 2770.1951 | 141.3877 | 2628.8074 | 2.4495 | 173.6421 | 6.202% | 6.202% | 5.839% | 0.7458% | 1.064% | 1.064% |  |  | 29.8049 | 173.6421
4074.003 | 16296.0121 | 3 | 800 | 3200 | 21.4747 | 3178.5253 | 11.5113 | 32.986 | 1.031% | 3167.014 | 142.5043 | 3024.5097 | 3.2425 | 178.7327 | 5.585% | 5.585% | 5.287% | 0.7677% | 1.031% | 1.031% |  |  | 32.986 | 178.7327
4583.2534 | 18333.0136 | 4 | 900 | 3600 | 22.0064 | 3577.9936 | 14.5865 | 36.5929 | 1.016% | 3563.4071 | 143.7686 | 3419.6385 | 4.145 | 184.5066 | 5.125% | 5.125% | 4.879% | 0.7984% | 1.016% | 1.016% |  |  | 36.5929 | 184.5066
5092.5038 | 20370.0151 | 5 | 1000 | 4000 | 22.6007 | 3977.3993 | 18.0248 | 40.6255 | 1.016% | 3959.3745 | 145.1803 | 3814.1943 | 5.1567 | 190.9625 | 4.774% | 4.774% | 4.571% | 0.8352% | 1.016% | 1.016% |  |  | 40.6255 | 190.9625
5601.7541 | 22407.0166 | 6 | 1100 | 4400 | 23.2575 | 4376.7425 | 21.826 | 45.0835 | 1.025% | 4354.9165 | 146.7388 | 4208.1777 | 6.277 | 198.0993 | 4.502% | 4.502% | 4.335% | 0.8765% | 1.025% | 1.025% |  |  | 45.0835 | 198.0993
6111.0045 | 24444.0181 | 7 | 1200 | 4800 | 23.9768 | 4776.0232 | 25.9899 | 49.9668 | 1.041% | 4750.0332 | 148.4437 | 4601.5896 | 7.5056 | 205.916 | 4.29% | 4.29% | 4.155% | 0.9212% | 1.041% | 1.041% |  |  | 49.9668 | 205.916
6620.2549 | 26481.0196 | 8 | 1300 | 5200 | 24.7588 | 5175.2412 | 30.5164 | 55.2752 | 1.063% | 5144.7248 | 150.2944 | 4994.4304 | 8.8418 | 214.4114 | 4.123% | 4.123% | 4.016% | 0.9684% | 1.063% | 1.063% |  |  | 55.2752 | 214.4114
7129.5053 | 28518.0211 | 9 | 1400 | 5600 | 25.6032 | 5574.3968 | 35.4053 | 61.0085 | 1.089% | 5538.9915 | 152.2906 | 5386.7008 | 10.2852 | 223.5844 | 3.993% | 3.993% | 3.91% | 1.018% | 1.089% | 1.089% |  |  | 61.0085 | 223.5844
7638.7557 | 30555.0226 | 10 | 1500 | 6000 | 26.5103 | 5973.4897 | 40.6564 | 67.1666 | 1.119% | 5932.8334 | 154.4318 | 5778.4016 | 11.8354 | 233.4338 | 3.891% | 3.891% | 3.831% | 1.068% | 1.119% | 1.119% |  |  | 67.1666 | 233.4338
8148.006 | 32592.0241 | 11 | 1600 | 6400 | 27.4798 | 6372.5202 | 46.2695 | 73.7493 | 1.152% | 6326.2507 | 156.7174 | 6169.5333 | 13.4919 | 243.9586 | 3.812% | 3.812% | 3.773% | 1.121% | 1.152% | 1.152% |  |  | 73.7493 | 243.9586
8657.2564 | 34629.0256 | 12 | 1700 | 6800 | 28.512 | 6771.488 | 52.2445 | 80.7565 | 1.188% | 6719.2435 | 159.147 | 6560.0965 | 15.2541 | 255.1576 | 3.752% | 3.752% | 3.733% | 1.174% | 1.188% | 1.188% |  |  | 80.7565 | 255.1576
9166.5068 | 36666.0271 | 13 | 1800 | 7200 | 29.6067 | 7170.3933 | 58.5812 | 88.1879 | 1.225% | 7111.8121 | 161.7202 | 6950.092 | 17.1218 | 267.0298 | 3.709% | 3.709% | 3.708% | 1.228% | 1.225% | 1.225% | 0 | 0 | 88.1879 | 267.0298
9675.7572 | 38703.0286 | 14 | 1900 | 7600 | 30.7639 | 7569.2361 | 65.2795 | 96.0433 | 1.264% | 7503.9567 | 164.4363 | 7339.5203 | 19.0942 | 279.5739 | 3.679% | 3.692% | 3.695% | 1.283% | 1.264% | 1.277% | 1 | 1 | 97.0364 | 280.6126
10185.0075 | 40740.0301 | 15 | 2000 | 8000 | 31.9837 | 7968.0163 | 72.3391 | 104.3227 | 1.304% | 7895.6773 | 167.2951 | 7728.3821 | 21.1711 | 292.789 | 3.66% | 3.687% | 3.692% | 1.338% | 1.304% | 1.33% | 2 | 2 | 106.4134 | 294.9757
10694.2579 | 42777.0317 | 16 | 2100 | 8400 | 33.266 | 8366.734 | 79.7598 | 113.0259 | 1.346% | 8286.9741 | 170.296 | 8116.6781 | 23.352 | 306.6739 | 3.651% | 3.692% | 3.699% | 1.394% | 1.346% | 1.385% | 3 | 3 | 116.3187 | 310.1179
11203.5083 | 44814.0332 | 17 | 2200 | 8800 | 34.6109 | 8765.3891 | 87.5417 | 122.1526 | 1.388% | 8677.8474 | 173.4385 | 8504.4089 | 25.6363 | 321.2274 | 3.65% | 3.705% | 3.713% | 1.451% | 1.388% | 1.44% | 4 | 4 | 126.7521 | 326.0381
11712.7587 | 46851.0347 | 18 | 2300 | 9200 | 36.0184 | 9163.9816 | 95.6843 | 131.7027 | 1.432% | 9068.2973 | 176.7222 | 8891.5751 | 28.0236 | 336.4485 | 3.657% | 3.725% | 3.735% | 1.508% | 1.432% | 1.497% | 5 | 5 | 137.7134 | 342.7352
12222.009 | 48888.0362 | 19 | 2400 | 9600 | 37.4884 | 9562.5116 | 104.1877 | 141.6761 | 1.476% | 9458.3239 | 180.1466 | 9278.1774 | 30.5135 | 352.3362 | 3.67% | 3.752% | 3.762% | 1.565% | 1.476% | 1.554% | 6 | 6 | 149.2025 | 360.2082
12731.2594 | 50925.0377 | 20 | 2500 | 10000 | 39.0209 | 9960.9791 | 113.0515 | 152.0725 | 1.521% | 9847.9275 | 183.7112 | 9664.2163 | 33.1055 | 368.8892 | 3.689% | 3.785% | 3.794% | 1.623% | 1.521% | 1.612% | 7 | 7 | 161.2191 | 378.4559
13240.5098 | 52962.0392 | 21 | 2600 | 10400 | 40.6161 | 10359.3839 | 122.2757 | 162.8918 | 1.566% | 10237.1082 | 187.4156 | 10049.6926 | 35.7992 | 386.1065 | 3.713% | 3.822% | 3.831% | 1.681% | 1.566% | 1.671% | 8 | 8 | 173.7632 | 397.4772
13749.7602 | 54999.0407 | 22 | 2700 | 10800 | 42.2737 | 10757.7263 | 131.8601 | 174.1338 | 1.612% | 10625.8662 | 191.2593 | 10434.6069 | 38.594 | 403.987 | 3.741% | 3.864% | 3.872% | 1.739% | 1.612% | 1.73% | 9 | 9 | 186.8346 | 417.271
14259.0106 | 57036.0422 | 23 | 2800 | 11200 | 43.9939 | 11156.0061 | 141.8045 | 185.7984 | 1.659% | 11014.2016 | 195.2418 | 10818.9598 | 41.4895 | 422.5297 | 3.773% | 3.909% | 3.917% | 1.798% | 1.659% | 1.79% | 10 | 10 | 200.4331 | 437.8363
14768.2609 | 59073.0437 | 24 | 2900 | 11600 | 45.7767 | 11554.2233 | 152.1087 | 197.8854 | 1.706% | 11402.1146 | 199.3627 | 11202.752 | 44.4853 | 441.7333 | 3.808% | 3.958% | 3.965% | 1.856% | 1.706% | 1.85% | 11 | 11 | 214.5584 | 459.172
15277.5113 | 61110.0452 | 25 | 3000 | 12000 | 47.622 | 11952.378 | 162.7725 | 210.3945 | 1.753% | 11789.6055 | 203.6215 | 11585.984 | 47.5809 | 461.5969 | 3.847% | 4.011% | 4.016% | 1.915% | 1.753% | 1.91% | 12 | 12 | 229.2105 | 481.2769
15786.7617 | 63147.0467 | 26 | 3100 | 12400 | 49.5299 | 12350.4701 | 173.7958 | 223.3258 | 1.801% | 12176.6742 | 208.0177 | 11968.6565 | 50.7759 | 482.1194 | 3.888% | 4.066% | 4.07% | 1.974% | 1.801% | 1.971% | 13 | 13 | 244.3892 | 504.1501
16296.0121 | 65184.0482 | 27 | 3200 | 12800 | 51.5003 | 12748.4997 | 185.1785 | 236.6788 | 1.849% | 12563.3212 | 212.5509 | 12350.7702 | 54.0699 | 503.2996 | 3.932% | 4.123% | 4.126% | 2.033% | 1.849% | 2.032% | 14 | 14 | 260.0943 | 527.7903
16805.2624 | 67221.0497 | 28 | 3300 | 13200 | 53.5333 | 13146.4667 | 196.9203 | 250.4536 | 1.897% | 12949.5464 | 217.2206 | 12732.3257 | 57.4623 | 525.1365 | 3.978% | 4.183% | 4.184% | 2.092% | 1.897% | 2.093% | 15 | 15 | 276.3256 | 552.1965
17314.5128 | 69258.0513 | 29 | 3400 | 13600 | 55.6289 | 13544.3711 | 209.0211 | 264.65 | 1.946% | 13335.35 | 222.0264 | 13113.3236 | 60.9527 | 547.6291 | 4.027% | 4.245% | 4.244% | 2.152% | 1.946% | 2.155% | 16 | 16 | 293.083 | 577.3677
17823.7632 | 71295.0528 | 30 | 3500 | 14000 | 57.787 | 13942.213 | 221.4807 | 279.2676 | 1.995% | 13720.7324 | 226.9678 | 13493.7645 | 64.5407 | 570.7761 | 4.077% | 4.309% | 4.307% | 2.211% | 1.995% | 2.217% | 17 | 17 | 310.3663 | 603.3028
18333.0136 | 73332.0543 | 31 | 3600 | 14400 | 60.0076 | 14339.9924 | 234.2989 | 294.3065 | 2.044% | 14105.6935 | 232.0444 | 13873.6491 | 68.2258 | 594.5767 | 4.129% | 4.375% | 4.37% | 2.271% | 2.044% | 2.279% | 18 | 18 | 328.1753 | 630.0007
18842.2639 | 75369.0558 | 32 | 3700 | 14800 | 62.2908 | 14737.7092 | 247.4756 | 309.7664 | 2.093% | 14490.2336 | 237.2556 | 14252.978 | 72.0076 | 619.0296 | 4.183% | 4.442% | 4.436% | 2.331% | 2.093% | 2.341% | 19 | 19 | 346.5099 | 657.4602
19351.5143 | 77406.0573 | 33 | 3800 | 15200 | 64.6366 | 15135.3634 | 261.0106 | 325.6471 | 2.142% | 14874.3529 | 242.601 | 14631.7519 | 75.8857 | 644.1338 | 4.238% | 4.511% | 4.503% | 2.39% | 2.142% | 2.404% | 20 | 20 | 365.3698 | 685.6805
19860.7647 | 79443.0588 | 34 | 3900 | 15600 | 67.0449 | 15532.9551 | 274.9037 | 341.9486 | 2.192% | 15258.0514 | 248.0802 | 15009.9713 | 79.8596 | 669.8883 | 4.294% | 4.581% | 4.571% | 2.45% | 2.192% | 2.466% | 21 | 21 | 384.755 | 714.6603
21261.2032 | 85044.8129 |  | 4175 | 16700 | 73.9902 | 16626.0098 | 314.955 | 388.9452 | 2.329% | 16311.0548 | 263.8339 | 16047.2209 | 91.2782 | 744.0573 | 4.455% | 4.756% | 4.764% | 2.615% | 2.329% | 2.616% | 22 | 22
9290 | 37160 |  | 1824.25 | 7297
15 min | ERCOT |  | 15 min | CNP |  | 7267 | AAL for CNP is measured at the Dist Fdr Bkr (PELCAR - Column G) so this value is increased accordingly for the high side of the sub trfs, Column E | [9 empty] | Secondary | Primary | CenterPoint Energy
|  |  |  | 7297 | 29.8815 | 7267.1185 | 60.1723 | 90.0539 | 1.234% | 7206.9461 | 162.3657 | 7044.5804 | 17.5905 | 270.0101 | 3.7%
9290 | 37160 | AAL | 1824.25 | 7297 | 29.8815 | 7267.1185 | 60.1723 | 90.0539 | 1.234% | 7206.9461 | 162.3657 | 7044.5804 | 17.5905 | 270.0101 | 3.7% |  | 3.704% | 1.241% | At ERCOT AAL
16915.75 | 67663 | Peak | 3687 | 14748 | 61.9905 | 14686.0095 | 245.7424 | 307.7328 | 2.087% | 14440.2672 | 236.5705 | 14203.6967 | 71.5105 | 615.8138 | 4.176% |  | 4.197% | 2.105% | At ERCOT Peak
|  |  |  | 14748 | 61.9905 | 14686.0095 | 245.7424 | 307.7328 | 2.087% | 14440.2672 | 236.5705 | 14203.6967 | 71.5105 | 615.8138 | 4.176%
18776.0614 | [5 empty] | 14686 | Peak for CNP is measured at the Dist Fdr Bkr (PELCAR - Column G) so this value is increased accordingly for the high side of the sub trfs, Column E
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately ---> | [14 empty] | Scaling for % Losses |  |  | 2013
(When ERCOT is at peak, CNP is 4 intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | Secondary | Primary |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor |  |  | 0.205% | 0.196% |  | Secondary Constants
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant
|  |  | 2013 Values ----> | 19.473 | 1.9548e-07 | 0 | 1.1394e-06 |  |  | 137.751 | 4.7391e-07 | 0 | 3.5446e-07 | <--- 2013 Values
|  |  | 2012 Values ----> | 21.1118 | 1.8286e-07 | 0 | 1.1394e-06 |  |  | 133.986 | 5.0407e-07 | 0 | 3.5446e-07 | <--- 2012 Values
|  |  | 2009 Values ----> | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  |  | 130.794 | 5.041e-07 | 0 | 3.5446e-07 | <--- 2009 Values
|  |  | 2008 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.01687 | right
|  |  | 2007 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | 0.000395 | middle
[17 empty] | F3 = | 0.01977 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001 |  |  |  | For Primary Distribution Customers "E"
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006 |  |  |  | Primary Constants
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value |  |  | F1 = | 0.011192 | right
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated | [6 empty] | F2 = | 1e-05 | middle
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review. | [6 empty] | F3 = | 0.00121 | left
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 9,304 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below and to the right)
2013
Secondary Constants
F1 = | 0.01687 | right
F2 = | 0.000395 | middle
F3 = | 0.01977 | left

## 3) Loss Equations
System Loss Equations For CenterPoint Energy for 2014 DLF
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
| 70.876 = | A * (16216 * 16216) + 19.280 |  |  |  |  | 70.876
| A = | 1.9548e-07 |  |  |  |  | 19.473
| B = | 19.473 | Total No-Load Losses For Substation Transformers = 19.280 MW |  |  |  | 51.403
Total Load Losses = 51.403 MW at 16,216 MW load level
[6 empty] | 2013 for use in 2014 | 16216
[5 empty] | No Load Losses | 19.473 | 16216
[5 empty] | Load Losses | 51.403 | 262958656
[5 empty] | Total | 70.876
1.9548e-07
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Distribution Transformers
| 236.573 = | A * (14,440.45 * 14,440.45) + 137.751
| A = | 4.7391e-07 | Total No-Load Losses For Distribution Transformers = 137.751 MW
| B = | 137.751 | Total Load Losses = 98.822 MW at 14,440.45 MW input to Dist Trfs
|  |  |  | 2013 |  | Corresponds to CNP load at Dist Bkrs of 14,686.20
|  | No Load Losses |  | 137.751 |  | Corresponds to CNP load at high side of sub trfs of 14,748.00
|  | Load Losses |  | 98.822
|  | Total |  | 236.573 | Information from DLF - 2013 Dist Trf Summary for DLF Calculation Rev3.xlsx
Secondary Conductor
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified