## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2013_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2013 as of 12/06/2012
Data from Seasonal SSWG Base Cases Updated with updates received by 12/06/2012
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2013_SPG1 | 61867.7 | 60639.3 | 1228.4 | 1227.37 | 1165.6 | 2254.7 | 48.84 | 49.76 | 1138.86 | 4164 | 4678 | 34.65 | 41.04 | 555.04 | 169 | 383 | 2.97 | 2.99 | 216.99 | 26 | 65.2 | 0.18 | 0.18 | 39.38 | 0 | 317.7 | 1.48 | 1.48 | 319.18 | 67 | 292 | 1.04 | 1.1 | 226.1 | 162 | 320.3 | 3.17 | 3.61 | 161.91 | 0 | 159 | 0.19 | 0.19 | 159.19
Spring Off Peak | 2013_SPG2 | 38172.8 | 37333.1 | 839.7 | 839.03 | 150 | 1297.4 | 17.25 | 17.25 | 1164.65 | 3887 | 2432 | 23.47 | 28.99 | -1426.01 | 66 | 171 | 0.96 | 0.96 | 105.96 | 49 | 40.8 | 0.12 | 0.13 | -8.07 | 0 | 151.1 | 0.17 | 0.17 | 151.27 | 0 | 142 | 0.38 | 0.38 | 142.38 | 40 | 199.8 | 1.44 | 1.44 | 161.24 | 0 | 76.3 | 0.06 | 0.06 | 76.36
Summer On Peak | 2013_SUM1 | 77913.2 | 76273.8 | 1629.88 | 1628.43 | 1441 | 2574.4 | 57.39 | 58.84 | 1192.24 | 4743 | 5420.8 | 43.28 | 51.82 | 729.62 | 289 | 502 | 6.23 | 6.26 | 219.26 | 91 | 110 | 0.73 | 0.8 | 19.8 | 0 | 352.8 | 2.21 | 2.21 | 355.01 | 89 | 315.1 | 1.21 | 1.29 | 227.39 | 246 | 405.4 | 5.26 | 5.88 | 165.28 | 0 | 214.6 | 0.28 | 0.28 | 214.88
Summer Off Peak | 2013_SUM2 | 45108.7 | 443345 | 763.76 | 763.03 | 271 | 1419.3 | 16.21 | 16.47 | 1164.77 | 2850 | 2927.1 | 15.38 | 19.28 | 96.38 | 48 | 153 | 0.85 | 0.85 | 105.85 | 91 | 67.3 | 0.38 | 0.43 | -23.27 | 0 | 179.9 | 0.7 | 0.7 | 180.6 | 46 | 168 | 0.33 | 0.45 | 122.45 | 40 | 240.8 | 2.14 | 2.14 | 202.94 | 0 | 85.2 | 0.09 | 0.09 | 85.29
Fall On Peak | 2013_FAL1 | 60391.8 | 59164.2 | 1227.53 | 1226.5 | 1008.2 | 2124.9 | 41.59 | 42.69 | 1159.39 | 3972 | 4086.1 | 29.5 | 35.4 | 149.5 | 97 | 312 | 1.91 | 1.91 | 216.91 | 49 | 94.8 | 0.42 | 0.43 | 46.23 | 0 | 285.1 | 0.87 | 0.87 | 285.97 | 57 | 283.9 | 1.06 | 1.06 | 227.96 | 198 | 318.5 | 3.19 | 3.75 | 124.25 | 0 | 147.2 | 0.17 | 0.17 | 147.37
Fall Off Peak | 2013_FAL2 | 36779.6 | 35988.9 | 790.76 | 789.73 | 53 | 1170.4 | 16.37 | 16.37 | 1133.77 | 2647 | 2083.6 | 13.88 | 17.8 | -545.6 | 30 | 135 | 0.54 | 0.55 | 105.55 | 26 | 59.1 | 0.15 | 0.15 | 33.25 | 0 | 119.7 | 0.15 | 0.15 | 119.85 | 15 | 133.8 | 0.29 | 0.29 | 119.09 | 11 | 172.6 | 1.13 | 1.13 | 162.73 | 0 | 64.2 | 0.06 | 0.06 | 64.26
Winter On Peak | 2014_WIN1 | 66313.2 | 64705.1 | 1608.15 | 1607.12 | 719.3 | 1819.4 | 43.74 | 44.13 | 1144.23 | 4621 | 4378.3 | 34.88 | 42.95 | -199.75 | 181 | 409.2 | 3.61 | 3.63 | 231.83 | 0 | 76.5 | 0.21 | 0.21 | 76.71 | 0 | 230.8 | 1.24 | 1.24 | 232.04 | 45 | 272 | 1.19 | 1.31 | 228.31 | 198 | 328.4 | 3.21 | 3.77 | 134.17 | 0 | 117.9 | 0.12 | 0.12 | 118.02
Winter Off Peak | 2014_WIN2 | 42556.6 | 41672.4 | 884.11 | 883.07 | 451.6 | 1394.4 | 23.14 | 23.4 | 966.2 | 3824.7 | 2933.3 | 22.71 | 28.05 | -863.35 | 53 | 167.8 | 0.78 | 0.78 | 115.58 | 0 | 44.8 | 0.07 | 0.07 | 44.87 | 0 | 117.7 | 0.43 | 0.43 | 118.13 | 51 | 172 | 0.37 | 0.38 | 121.38 | 64 | 215.5 | 1.3 | 1.31 | 152.81 | 0 | 55.3 | 0.04 | 0.04 | 55.34
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2013_SPG1 | 2517 | 1086.76 | 460 | 40 | 129.4 | 0 | 4233.16 |  | 8469.9 | 2816.65 | 5653.25 | 92.52 | 2013_SPG1
Spring Off Peak | 2013_SPG2 | 2517 | 1086.76 | 460 | 40 | 129.4 | 0 | 4233.16 |  | 4510.4 | 367.78 | 4142.62 | 43.85 | 2013_SPG2
Summer On Peak | 2013_SUM1 | 2517 | 1318.17 | 460 | 40 | 129.4 | 0 | 4464.57 |  | 9895.1 | 3123.48 | 6771.62 | 116.59 | 2013_SUM1
Summer Off Peak | 2013_SUM2 | 2517 | 1086.76 | 460 | 40 | 129.4 | 0 | 4233.16 |  | 5240.6 | 1935.01 | 3305.59 | 36.08 | 2013_SUM2
Fall On Peak | 2013_FAL1 | 2517 | 1093.19 | 460 | 40 | 129.4 | 0 | 4239.59 |  | 7652.5 | 2357.58 | 5294.92 | 78.71 | 2013_FAL1
Fall Off Peak | 2013_FAL2 | 2517 | 1086.76 | 460 | 11 | 129.4 | 0 | 4204.16 |  | 3938.4 | 1192.9 | 2745.5 | 32.57 | 2013_FAL2
Winter On Peak | 2014_WIN1 | 2517 | 1153.65 | 460 | 40 | 129.4 | 0 | 4300.05 |  | 7632.5 | 1965.56 | 5666.94 | 88.2 | 2014_WIN1
Winter Off Peak | 2014_WIN2 | 2517 | 1108.71 | 460 | 40 | 129.4 | 0 | 4255.11 |  | 5100.8 | 710.96 | 4389.84 | 48.84 | 2014_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 57634.54 | 33939.64 | 2.131% | 2.474% |  | 2254.7 | 1297.4 | 2.12% | 1.312% |  | 4678 | 2432 | 0.7353% | 0.9558% |  | 383 | 171 | 0.7695% | 0.5583% |  | 65.2 | 40.8 | 0.2753% | 0.2933% |  | 317.7 | 151.1 | 0.4637% | 0.1124% |  | 292 | 142 | 0.3549% | 0.2669% |  | 320.3 | 199.8 | 0.98% | 0.7156% |  | 159 | 76.3 | 0.1194% | 0.07858%
SUMMER | 73448.63 | 40875.54 | 2.219% | 1.869% |  | 2574.4 | 1419.3 | 2.181% | 1.129% |  | 5420.8 | 2927.1 | 0.7921% | 0.5227% |  | 502 | 153 | 1.226% | 0.5525% |  | 110 | 67.3 | 0.6593% | 0.5615% |  | 352.8 | 179.9 | 0.6225% | 0.3876% |  | 315.1 | 168 | 0.3825% | 0.196% |  | 405.4 | 240.8 | 1.281% | 0.8809% |  | 214.6 | 85.2 | 0.1303% | 0.1055%
FALL | 56152.21 | 32575.44 | 2.186% | 2.427% |  | 2124.9 | 1170.4 | 1.92% | 1.379% |  | 4086.1 | 2083.6 | 0.7168% | 0.6617% |  | 312 | 135 | 0.6085% | 0.3984% |  | 94.8 | 59.1 | 0.4411% | 0.2532% |  | 285.1 | 119.7 | 0.3042% | 0.1252% |  | 283.9 | 133.8 | 0.372% | 0.2163% |  | 318.5 | 172.6 | 0.9916% | 0.6504% |  | 147.2 | 64.2 | 0.1154% | 0.09337%
WINTER | 62013.15 | 38301.49 | 2.593% | 2.308% |  | 1819.4 | 1394.4 | 2.348% | 1.632% |  | 4378.3 | 2933.3 | 0.7904% | 0.7683% |  | 409.2 | 167.8 | 0.8745% | 0.4627% |  | 76.5 | 44.8 | 0.2738% | 0.156% |  | 230.8 | 117.7 | 0.5344% | 0.364% |  | 272 | 172 | 0.4356% | 0.2147% |  | 328.4 | 215.5 | 0.968% | 0.5996% |  | 117.9 | 55.3 | 0.1017% | 0.07228%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | -1.4465e-05 | 2.965 |  |  |  | 0.00084412 | 0.21697 |  |  |  | -9.8206e-05 | 1.1947 |  |  |  | 0.00099632 | 0.3879 |  |  |  | -0.00073531 | 0.32326 |  |  |  | 0.0021087 | -0.20624 |  |  |  | 0.00058673 | 0.18358 |  |  |  | 0.0021945 | 0.27711 |  |  |  | 0.0004931 | 0.040952
SUMMER | 1.0763e-05 | 1.4286 |  |  |  | 0.00091025 | -0.1627 |  |  |  | 0.00010803 | 0.20647 |  |  |  | 0.0019293 | 0.2573 |  |  |  | 0.0022903 | 0.40733 |  |  |  | 0.0013587 | 0.14317 |  |  |  | 0.0012678 | -0.016946 |  |  |  | 0.0024301 | 0.29572 |  |  |  | 0.00019152 | 0.089205
FALL | -1.0239e-05 | 2.761 |  |  |  | 0.00056608 | 0.71684 |  |  |  | 2.7485e-05 | 0.60448 |  |  |  | 0.0011867 | 0.2382 |  |  |  | 0.0052638 | -0.057929 |  |  |  | 0.0010827 | -0.0044375 |  |  |  | 0.0010374 | 0.077472 |  |  |  | 0.0023386 | 0.24679 |  |  |  | 0.00026488 | 0.076365
WINTER | 1.2017e-05 | 1.848 |  |  |  | 0.0016829 | -0.71427 |  |  |  | 1.529e-05 | 0.72341 |  |  |  | 0.0017059 | 0.17644 |  |  |  | 0.0037146 | -0.010407 |  |  |  | 0.0015065 | 0.18669 |  |  |  | 0.0022094 | -0.16536 |  |  |  | 0.0032628 | -0.10351 |  |  |  | 0.0004696 | 0.046311
EFFECTIVE DATES | SEASON
03/01/13 - 05/31/13 | SPRING
06/01/13 - 09/30/13 | SUMMER
10/01/13 - 11/30/13 | FALL
12/01/13 - 02/28/14 | WINTER