## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2014_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2014 as of 12/30/13
Data from Seasonal SSWG Base Cases Updated with updates received by 12/30/13
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2014_SPG1 | 63645.6 | 62266.9 | 1275.82 | 1275.82 | 1141 | 2435 | 42 | 42.58 | 1336.58 | 4379 | 4550 | 35.69 | 42.67 | 213.67 | 136 | 351 | 2.78 | 2.79 | 217.79 | 26 | 66.4 | 0.16 | 0.16 | 40.56 | 0 | 318.1 | 0.92 | 0.92 | 319.02 | 80 | 308 | 1.03 | 1.15 | 229.15 | 81 | 321.7 | 3.44 | 3.53 | 244.23 | 0 | 145 | 0.31 | 0.31 | 145.31
Spring Off Peak | 2014_SPG2 | 38267.5 | 37610.4 | 602.15 | 602.17 | 82 | 1216.3 | 12.71 | 12.8 | 1147.1 | 2907 | 2325 | 14.75 | 18.7 | -563.3 | 52 | 157 | 0.57 | 0.57 | 105.57 | 49 | 41.5 | 0.12 | 0.12 | -7.38 | 0 | 198.4 | 0.36 | 0.36 | 198.76 | 34 | 156 | 0.3 | 0.37 | 122.37 | 57 | 193.9 | 1.42 | 1.49 | 138.39 | 0 | 65.2 | 0.06 | 0.06 | 65.26
Summer On Peak | 2014_SUM1 | 78438.7 | 76741.2 | 1563.43 | 1565.37 | 1091 | 2730 | 58.15 | 59.21 | 1698.21 | 4743 | 5305 | 43.01 | 51.48 | 613.48 | 294 | 507 | 5.89 | 5.9 | 218.9 | 91 | 112 | 0.67 | 0.72 | 21.72 | 0 | 353.4 | 1.24 | 1.24 | 354.64 | 104 | 333.9 | 1.11 | 1.24 | 231.14 | 266 | 369.7 | 4.69 | 5.65 | 109.35 | 0 | 208.6 | 0.32 | 0.32 | 208.92
Summer Off Peak | 2014_SUM2 | 46924.3 | 46184.6 | 673.99 | 674.6 | 100 | 1433.4 | 19.61 | 19.62 | 1353.02 | 3055 | 2797 | 15.78 | 20.01 | -237.99 | 49 | 154 | 0.99 | 0.99 | 105.99 | 91 | 68.4 | 0.36 | 0.4 | -22.2 | 0 | 180.2 | 0.39 | 0.39 | 180.59 | 46 | 169 | 0.31 | 0.43 | 123.43 | 81 | 216.9 | 1.43 | 1.5 | 137.4 | 0 | 94.2 | 0.11 | 0.11 | 94.31
Fall On Peak | 2014_FAL1 | 60158.5 | 58795.4 | 1258.3 | 1258.83 | 974.9 | 2290 | 37.39 | 38.15 | 1353.25 | 3177 | 4105 | 25.99 | 30.78 | 958.78 | 100 | 315 | 1.49 | 1.5 | 216.5 | 49 | 96.4 | 0.37 | 0.38 | 47.78 | 0 | 285.6 | 0.58 | 0.58 | 286.18 | 97 | 323 | 0.99 | 1.11 | 227.11 | 81 | 363.6 | 4.33 | 4.44 | 287.04 | 0 | 152.2 | 0.25 | 0.25 | 152.45
Fall Off Peak | 2014_FAL2 | 37269.3 | 36647.8 | 567.52 | 567.66 | 0 | 1094.2 | 15.32 | 15.32 | 1109.52 | 2987 | 2135 | 13.66 | 17.82 | -834.18 | 32 | 137 | 0.37 | 0.37 | 105.37 | 26 | 60.1 | 0.13 | 0.14 | 34.24 | 0 | 119.9 | 0.15 | 0.16 | 120.06 | 42 | 164 | 0.29 | 0.39 | 122.39 | 41 | 202.8 | 1.37 | 1.45 | 163.25 | 0 | 71.3 | 0.07 | 0.07 | 71.37
Winter On Peak | 2015_WIN1 | 63585.4 | 62041.9 | 1431.06 | 1431.68 | 739 | 2030.9 | 38.59 | 39.11 | 1331.01 | 3639 | 3956 | 26.96 | 32.78 | 349.78 | 185 | 399 | 2.89 | 2.91 | 216.91 | 0 | 77.8 | 0.17 | 0.17 | 77.97 | 0 | 220.3 | 0.41 | 0.41 | 220.71 | 57 | 284 | 1.04 | 1.04 | 228.04 | 81 | 258.1 | 3.03 | 3.13 | 180.23 | 0 | 148.8 | 0.18 | 0.18 | 148.98
Winter Off Peak | 2015_WIN2 | 43122 | 42302.1 | 751.16 | 751.7 | 362 | 1674.2 | 21.15 | 21.15 | 1333.35 | 2567.7 | 2622 | 19.76 | 20.39 | 74.69 | 54 | 164 | 0.89 | 0.89 | 110.89 | 0 | 45.6 | 0.06 | 0.06 | 45.66 | 0 | 112.4 | 0.23 | 0.23 | 112.63 | 22 | 144 | 0.26 | 0.29 | 122.29 | 81 | 183.7 | 1.36 | 1.4 | 104.1 | 0 | 86.1 | 0.06 | 0.06 | 86.16
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2014_SPG1 | 2567 | 1093.19 | 460 | 40 | 109.3 | 0 | 4269.49 |  | 8495.2 | 2746.31 | 5748.89 | 86.33 | 2014_SPG1
Spring Off Peak | 2014_SPG2 | 2567 | 1093.19 | 460 | 40 | 109.3 | 0 | 4269.49 |  | 4353.3 | 1206.77 | 3146.53 | 30.29 | 2014_SPG2
Summer On Peak | 2014_SUM1 | 2567 | 1353.92 | 460 | 40 | 109.3 | 0 | 4530.22 |  | 9919.6 | 3456.36 | 6463.24 | 115.08 | 2014_SUM1
Summer Off Peak | 2014_SUM2 | 2567 | 1093.19 | 460 | 40 | 109.3 | 0 | 4269.49 |  | 5113.1 | 1734.55 | 3378.55 | 38.98 | 2014_SUM2
Fall On Peak | 2014_FAL1 | 2567 | 1093.19 | 460 | 40 | 109.3 | 0 | 4269.49 |  | 7930.8 | 3529.09 | 4401.71 | 71.39 | 2014_FAL1
Fall Off Peak | 2014_FAL2 | 2567 | 1093.19 | 460 | 0 | 109.3 | 0 | 4229.49 |  | 3984.3 | 892.02 | 3092.28 | 31.36 | 2014_FAL2
Winter On Peak | 2015_WIN1 | 2567 | 1160.08 | 460 | 40 | 109.3 | 0 | 4336.38 |  | 7374.9 | 2753.63 | 4621.27 | 73.27 | 2015_WIN1
Winter Off Peak | 2015_WIN2 | 2567 | 1160.08 | 460 | 40 | 109.3 | 0 | 4336.38 |  | 5032 | 1989.77 | 3042.23 | 43.77 | 2015_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 59376.11 | 33998.01 | 2.149% | 1.771% |  | 2435 | 1216.3 | 1.696% | 1.034% |  | 4550 | 2325 | 0.7783% | 0.6304% |  | 351 | 157 | 0.7858% | 0.3617% |  | 66.4 | 41.5 | 0.2404% | 0.2883% |  | 318.1 | 198.4 | 0.2884% | 0.1811% |  | 308 | 156 | 0.3333% | 0.1919% |  | 321.7 | 193.9 | 1.058% | 0.727% |  | 145 | 65.2 | 0.2133% | 0.09194%
SUMMER | 73908.48 | 42654.81 | 2.115% | 1.58% |  | 2730 | 1433.4 | 2.086% | 1.35% |  | 5305 | 2797 | 0.8042% | 0.561% |  | 507 | 154 | 1.148% | 0.6388% |  | 112 | 68.4 | 0.5947% | 0.5236% |  | 353.4 | 180.2 | 0.3497% | 0.216% |  | 333.9 | 169 | 0.3313% | 0.1831% |  | 369.7 | 216.9 | 1.253% | 0.655% |  | 208.6 | 94.2 | 0.1532% | 0.1166%
FALL | 55889.01 | 33039.81 | 2.251% | 1.718% |  | 2290 | 1094.2 | 1.607% | 1.381% |  | 4105 | 2135 | 0.6291% | 0.6357% |  | 315 | 137 | 0.4708% | 0.2693% |  | 96.4 | 60.1 | 0.3823% | 0.2158% |  | 285.6 | 119.9 | 0.2027% | 0.1249% |  | 323 | 164 | 0.3056% | 0.1765% |  | 363.6 | 202.8 | 1.177% | 0.671% |  | 152.2 | 71.3 | 0.164% | 0.09808%
WINTER | 59249.02 | 38785.62 | 2.415% | 1.937% |  | 2030.9 | 1674.2 | 1.865% | 1.248% |  | 3956 | 2622 | 0.6769% | 0.748% |  | 399 | 164 | 0.7191% | 0.5398% |  | 77.8 | 45.6 | 0.218% | 0.1314% |  | 220.3 | 112.4 | 0.1858% | 0.2042% |  | 284 | 144 | 0.3649% | 0.1802% |  | 258.1 | 183.7 | 1.16% | 0.7349% |  | 148.8 | 86.1 | 0.1208% | 0.06964%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | 1.4878e-05 | 1.2653 |  |  |  | 0.00054274 | 0.37403 |  |  |  | 6.6464e-05 | 0.47588 |  |  |  | 0.0021859 | 0.018565 |  |  |  | -0.0019252 | 0.36822 |  |  |  | 0.00089608 | 0.0033416 |  |  |  | 0.00093002 | 0.046856 |  |  |  | 0.0025899 | 0.22482 |  |  |  | 0.0015213 | -0.0072466
SUMMER | 1.7126e-05 | 0.84959 |  |  |  | 0.00056764 | 0.53596 |  |  |  | 9.6975e-05 | 0.28977 |  |  |  | 0.0014437 | 0.41641 |  |  |  | 0.0016307 | 0.41202 |  |  |  | 0.00077189 | 0.076864 |  |  |  | 0.00089895 | 0.031173 |  |  |  | 0.0039119 | -0.19351 |  |  |  | 0.00031934 | 0.086555
FALL | 2.3359e-05 | 0.9459 |  |  |  | 0.00018878 | 1.1742 |  |  |  | -3.3493e-06 | 0.6429 |  |  |  | 0.0011317 | 0.1143 |  |  |  | 0.0045871 | -0.059844 |  |  |  | 0.00046905 | 0.068709 |  |  |  | 0.00081162 | 0.043411 |  |  |  | 0.0031458 | 0.033041 |  |  |  | 0.00081468 | 0.039994
WINTER | 2.339e-05 | 1.0295 |  |  |  | 0.0017303 | -1.6493 |  |  |  | -5.33e-05 | 0.88774 |  |  |  | 0.00076318 | 0.41459 |  |  |  | 0.0026903 | 0.00873 |  |  |  | -0.00017094 | 0.22342 |  |  |  | 0.0013188 | -0.009676 |  |  |  | 0.0057183 | -0.31556 |  |  |  | 0.00081633 | -0.00064787
EFFECTIVE DATES | SEASON
03/01/14 - 05/31/14 | SPRING
06/01/14 - 09/30/14 | SUMMER
10/01/14 - 11/30/14 | FALL
12/01/14 - 02/28/15 | WINTER