## Slide 1: Review of Reliability Performance Data
Texas Reliability Entity, Inc.

## Slide 2: Introduction
This purpose of the presentation is to review the performance data for the ERCOT region.
  Overview of the reliability areas of interest
  Review of key metrics for each area
  Review of key observations
Data is collected under Section 800, 1000 or 1600 of the NERC Rules of Procedure, not under Section 400 (compliance and enforcement).

## Slide 3: Texas RE Review of Reliability Performance
Texas RE Assessment of Reliability Performance report for 2013 planned for publication April 2014 will provide:
High-level 2013 data;
Associated historical data;
Analysis of 2013 and other historical data as indicators of current state of ERCOT region;
Observations that help connect the state of the region today to the future; and
Recommendations, where possible, for addressing threats to reliability and gaps in data and analysis process.
2012 Texas RE Assessment of Reliability Performance (May 2013): http://www.texasre.org/CPDL/2012%20Texas%20RE%20State%20of%20Reliability%20Report.pdf
NERC 2013 State of Reliability Report (May 2013): http://www.nerc.com/pa/RAPA/PA/Performance%20Analysis%20DL/2013_SOR_May%2015.pdf

## Slide 4: NERC Reliability Impact Steering Committee’s 2013 Risks and Challenges

## Slide 5: Reliability Areas with Associated Data
Event Analysis
Transmission Reliability Analysis (TADS)
Generation Reliability Analysis (GADS)
Protection System Misoperations
Frequency Control
Primary Frequency Response
Demand Response
Infrastructure Protection
Ancillary Service and Other Performance Trends

## Slide 6: Event Analysis – Key Observations 2011-2013
Eighty-nine (89) reportable events
  80 events classified as Category 0 or Category 1 (little or minimal follow-up per Events Analysis Program)
  304 event reports received
  94 lessons learned received
Weather (37%), Equipment Failure (34%), and Relaying Issues (9%) are the main causes
14 events in 2011-2013 involved multiple generator trips
Generation trips > 450 MW average 18 per quarter
  Boiler system (25 events), steam turbine/generator (21 events), external to plant (13 events), and balance of plant (49 events) are the major causes.

## Slide 7: Event Analysis – Summary Data
Weather (37%), Equipment Failure (34%), and Relaying Issues (9%) are the main causes of events

## Slide 8: Event Analysis – Summary Data
NERC metrics ALR6-2, ALR6-3, ALR2-5 and ALR2-5
Average three DCS events per year since 2008
Average four OE-417 reportable outage events per year with average customer impact of 490,000 per year

## Slide 9: Transmission Reliability – Key Observations
842 automatic outages and 2343 planned outages of 345kV lines reported in Transmission Data Availability System (TADS) for 2010-2013
  Overall average circuit availability remained above 98.5%.
  Lightning, Contamination, and Unknown represented 73% of momentary outages.
  Lightning, Failed Substation Equipment, and Human Error represented 50% of sustained outages.
  “Unknown” represents 20% of momentary outages. More accurate cause coding will help future analysis.
  “Failed AC Substation Equipment” represented 21% of sustained outage events and 25% of outage duration. “Failed AC Circuit Equipment” represented 7% of sustained outage events vs. 39% of outage duration. Sharing of lessons learned may reduce these events.
Dependent Mode and Common Mode outages merit deeper review
  Represented 8.1% of momentary outage events, 33.2% of sustained outage events and 49.1% of sustained outage duration for 2010-2013 combined
Initial review of voltage control performance in progress
Annual TADS summary is shared with OWG

## Slide 10: ERCOT Region TADS Data for 2011-2013
 | 2011 |  | 2012 |  | 2013 (thru Q3) | 
Outage Information | Count | Duration (hrs) | Count | Duration (hrs) | Count | Duration (hrs)
Automatic | 279 | 1908.6 | 230 | 682.6 | 139 | 1396.8
Non-Automatic | 787 | 46712.4 | 516 | 36295.1 | 467 | 39832.6
 | 2011 | 2012 | 2013 (thru Q3) | 2011 | 2012 | 2013 (thru Q3)
Voltage Class | 300-399 kV | 300-399 kV | 300-399 kV | 300-399 kV | 300-399 kV | 300-399 kV
Metric | Outages/Number of circuits |  |  | Outages/100 mi/year |  | 
AC Transmission Outages - Failed Protection System Equipment | 0.0305 | 0.0262 | 0.0204 | 0.0926 | 0.0804 | 0.0602
AC Transmission Outages - Human Error | 0.0677 | 0.0426 | 0.0175 | 0.2057 | 0.1307 | 0.0516
AC Transmission Outages - Failed AC Substation Equipment | 0.1320 | 0.0589 | 0.0204 | 0.4011 | 0.1809 | 0.0602
AC Transmission Outages - Failed AC Circuit Equipment | 0.0508 | 0.0458 | 0.0087 | 0.1543 | 0.1407 | 0.0258
AC Transmission Outages - Lightning | 0.2067 | 0.2055 | 0.1309 | 0.6376 | 0.6333 | 0.3872
AC Transmission Outages - Contamination | 0.1667 | 0.1011 | 0.1018 | 0.5142 | 0.3116 | 0.3011
AC Transmission Outages - Foreign Interference | 0.0567 | 0.0620 | 0.0029 | 0.1748 | 0.1910 | 0.0086
Total | 0.9300 | 0.7504 | 0.4112 | 2.8694 | 2.3121 | 1.1960
Element Availability Percentage (APC) | 98.0625 | 98.6192 | 98.6287 |  |  | 
Transmission System Unavailability | 1.9375 | 1.3808 | 1.3713 |  |  | 

## Slide 11: Transmission Availability – ALR Metrics
 |  | 2010 |  | 2011 |  | 2012 |  | 2013 (thru Q3) | 
Metric | Definition | ERCOT Metric | NERC Metric | ERCOT Metric | NERC Metric | ERCOT Metric | NERC Metric | ERCOT Metric | NERC Metric
ALR6-11 | Automatic Outages Initiated by Failed Protection Equipment | 4.95% | 6.26% | 3.05% | 5.55% | 2.62% | 5.19% | 2.04% | 3.43%
ALR6-12 | Automatic Outages Initiated by Human Error | 1.41% | 6.57% | 6.77% | 6.87% | 4.26% | 6.55% | 1.75% | 3.78%
ALR6-13 | Automatic Outages Initiated by Failed AC Substation Equipment | 8.13% | 5.59% | 13.2% | 8.14% | 5.89% | 6.19% | 2.04% | 2.66%
ALR6-14 | Automatic Outages Initiated by Failed AC Circuit Equipment | 2.83% | 5.89% | 5.08% | 5.37% | 4.58% | 5.01% | 0.87% | 1.89%
ALR6-15 | Element Availability Percentage | 98.64% | 98.41% | 98.06% | 97.86% | 98.62% | 97.89% | 98.63% | 98.94%
Comparison of ERCOT to NERC metrics for Adequate Level of Reliability (ALR) measurements for 300-399 kV

## Slide 12: Transmission Limits – IROL Exceedances
Count of Interconnection Reliability Operation Limit (IROL) exceedances, categorized by duration
West-North Exceedance for 13 minutes due to forced outages
West-North Exceedance for 11 minutes (Limit reduced due to unsolved contingencies. Transmission Watch issued)
NERC ALR 3-5 IROL/SOL Exceedance (< 30 minutes) |  | 
Region | 2011 | 2012
EI | 194 | 172
WECC | 734 | 927
TRE | 103 | 82
Note: IROL/SOL violations from 10 sec to < 30 minutes |  | 
Notes: Two IROLs (W-N and N-H).
Chart shows the count, by duration, of IROL exceedances for each quarter.
Also reported to NERC as part of ALR3-5.
W-N represents virtually all of these exceedances.
No exceedances > 20 minutes
Blue line shows total duration for the quarter of IROL exceedances.
Recent exceedances >10 min have explanations in yellow bubbles.

## Slide 13: Transmission Limits (Line Binding Constraints)
Lines represent the total number of lines which are a constraint during the month (i.e. a post-contingency overload > 100%)
Bars represent the total hours during the month that the line constraints occurred
Notes: Thermal limits.
Data source from MIS “Security violations and Binding Constraints”
File is sorted/filtered for post-contingency overloads > 100% of rating.
Lines represent # circuits with post-contingency overloads > 100% of rating.
Bars represent avg hours per circuit of constraint
Does not take into account if a RAP, SPS, MP, or TOAP is in place.

## Slide 14: Transmission Outages – Common/Dependent Mode
Common Mode and Dependent Mode Outage Statistics
Dependent Mode outages (defined as an automatic outage of an element which occurred as a result of another outage)
Common Mode outages (defined as one or more automatic outages with the same initiating cause and occur nearly simultaneously).
Common Mode & Dependent Mode Outage Comparison 2010-2013 (Q3) |  | 
 | TRE | NERC
Momentary Cause | 8.1% | 15.6%
Sustained Cause | 33.2% | 28.9%
Sustained Duration | 49.1% | 49.4%
Note: Multi-year average |  | 

## Slide 15: Voltage Control (Generation Buses) – Dec 2013
One-minute PI data from 52 generation buses (138kV and 345kV). Includes both fossil and wind generation.
Boxes represent the 25%/75% percentiles. Leader lines show the min/max voltage during the period.
Data is normalized so that the 1.0 per-unit value represents the control point from the seasonal voltage profile
Telemetry flat-lined since 11/25
Notes: TSP Planners derive target seasonal voltage profiles each year.
ERCOT protocols & guides require generators to be within 2% of their profile.
Chart shows 52 generation buses scattered throughout the system in relation to the seasonal voltage profile for the month.
Includes both wind and non-wind generators.
Data is normalized so that the 1.0 PU line represents the seasonal profile target.
Boxes show the 25%/75% iles. Leader lines show the min/max values.

## Slide 16: Voltage Control (Transmission Buses) – Dec 2013
One-minute PI data from 61 345kV transmission buses.
Boxes represent the 25%/75% percentiles. Leader lines show the min/max voltage during the period.

## Slide 17: Voltage Control by Weather Zone One-minute PI data from one selected generation bus in each weather zone, normalized from seasonal profile

## Slide 18: Generation Reliability – Key Observations
Mandatory GADS reporting for units > 50 MW began in Jan 2012
Mandatory GADS reporting for units > 20 MW (excluding wind) began Jan 2013
Immediate forced outage and forced de-rate events were reviewed for common failure modes
ERCOT-region GADS metrics compare favorably with NERC fleet-wide metrics in most cases
Quarterly GADS summary is shared with PDCWG

## Slide 19: Review of ERCOT-Region GADS Data
EFORd: Equivalent Forced Outage Rate Demand. Measures the probability that a unit will not meet its demand periods for generating requirements because of forced outages or derates.
ERCOT units only, based on GADS submittal data (no wind, or units under 50 MW in 2012)
NERC 2008-2012 Fleet Avg EFORd | 
Fossil | 9.71
Coal | 8.29
Gas | 16.63
Lignite | 6.99
Nuclear | 3.94
Jet Engine | 9.87
Gas Turbine | 10.49
CC Block | 4.57

## Slide 20: Review of ERCOT-Region GADS Data
Equivalent Availability Factor: Measures the percentage of net maximum generation that could be provided after all types of outages are taken into account. Weighted by unit MW capacity.
ERCOT units only, based on GADS submittal data (no wind, or units under 50 MW in 2012)
NERC 2008-2012 Fleet Avg WEAF | 
Fossil | 82.90
Coal | 83.08
Gas | 82.82
Lignite | 84.80
Nuclear | 87.66
Jet Engine | 89.14
Gas Turbine | 90.15
CC Block | 86.63
Notes: Important metric for consideration in reserve margin calculations

## Slide 21: Review of GADS Forced Outage Data
Major System | Number of Immediate Forced Outage events 2012 and 2013 (thru Q3) | Total Duration (hrs) | Avg Duration per Event (hrs)
Boiler System | 419 | 17823.8 | 42.5
Nuclear Reactor | 1 | 226.9 | 226.9
Balance of Plant | 658 | 23671.4 | 36.0
Steam Turbine/Generator | 641 | 52916.9 | 82.6
Gas Turbine/ Jet Engine/Expander | 1011 | 40525.7 | 40.1
Heat Recovery Steam Generator/Other Combined Cycle | 91 | 4047.3 | 44.5
Pollution Control Equipment | 50 | 1068.9 | 21.4
External | 135 | 3115.5 | 23.1
Regulatory, Safety, Environmental | 12 | 9081.3 | 756.8
Personnel/Procedure Errors | 83 | 562.4 | 6.8

## Slide 22: Protection System Misoperations – Key Observations
Relatively flat trend in overall misoperation rate since Jan 2011
  2011 overall rate of 8.85% compared to 2012 overall rate of 9.99% and 2013 rate (thru Q3) of 8.31%
  Slight upward trend in 345kV rate of 9.01% in 2011 compared to 2012 345kV rate of 11.34% and 2013 rate (thru Q3) of 12.30%
Incorrect settings/logic (43%), Relay failure (21%), and Communications failure (10%) are the main causes. This is similar to NERC-wide trend.
  Relay failures evenly split between electromechanical and microprocessor-based relay systems
Transmission lines (62%), Transformers (12%), and Generators (10%) are the main facilities affected by misoperations
  83% of generator misoperations occur with no system fault
52% of misoperations attributable to “human” performance
Quarterly misoperation summaries are shared with SPWG

## Slide 23: ERCOT Region Protection System Misoperations
Lines show percentage of protection system operations that are misoperations, including Failure to Reclose
Percent Misoperation Rate is normalized based on number of system events
NERC 2013 Q1/Q2 Misoperation Rates |  | 
Region | Q1 | Q2
FRCC | 12.8% | 13%
MRO | 12.6% | 11%
NPCC | 7.2% | 7%
RFC | 16.9% | 17%
SERC | 8.9% | 9%
SPP | 14.3% | 13%
TRE | 8.9% | 8%
Note: NERC misoperation rates do not include Failure to Reclose. |  | 

## Slide 24: ERCOT Region “Human Error” Misoperation Reports
Percentage of Protection System Misoperations due to human factors, i.e. settings errors, wiring errors, design errors, etc.

## Slide 25: Frequency Control and Primary Frequency Response – Key Observations
Frequency profile has narrowed slightly since start of nodal market. However, it has also shifted higher (to approximately 60.015 Hz), in part due to impact of governor response from wind generators for high frequencies.
For 2012, time error corrections averaged 9.4 per month (or an average of one (1) second of per day), always for slow time error. For 2013, time error corrections averaged 1.8 each month with zero corrections from July thru November.
Long term trends for primary frequency response show improvement.
Some issues with non-frequency responsive units providing Responsive Reserve Service.
Regulation exhaustion rates have shown improvement since implementation of SCR773.
NERC recalculated the BAL-003-1 frequency response obligation from 286 MW per 0.1 Hz to 412 MW per 0.1 Hz.

## Slide 26: Frequency Control
Bars represent % of time that frequency is outside 30 mHz Epsilon-1 (ε1) value which is used calculation of CPS 1 for the ERCOT region per BAL-001 (i.e. < 59.97 Hz or > 60.03 Hz)
Based on one-minute PI data
NERC CPS1 Performance | 
Eastern-2010 | 130
Eastern-2011 | 128
Eastern-2012 | 130
Western-2010 | 165
Western-2011 | 155
Western-2012 | 147
ERCOT-2010 | 150
ERCOT-2011 | 148
ERCOT-2012 | 160
ERCOT-2013 YTD | 166

## Slide 27: Primary Frequency Response Performance
Primary Frequency Response provided by generating units during loss of generation events is showing an improving trend since summer 2012.
ERCOT target is 420 MW per 0.1 Hz (green line). NERC minimum is 286 MW per 0.1 Hz (red line) per BAL-003-1 for 2013 (Will change to 412 MW per 0.1 Hz for 2014)
Leader lines show min/max for the quarter.
Boxes indicate 25%/75% quartiles.

## Slide 28: Demand Response, Infrastructure Protection, and Ancillary Service Performance – Observations
Demand Response
  Reported demand response capacity increased by 25% since January 2013, to ~ 6000 MW as of Sept 2013
Infrastructure Protection
  Texas RE monitors reports from the System Security Response Group (SSRG)
  Since Jan 2011, reports of copper theft and substation intrusion have averaged 12 per month, with a maximum of 28 in one month
Ancillary Service/Other Performance issues
  Some failure of entities to maintain adequate capacity to cover ancillary service obligations
  Some generators not current with required reactive tests
  Some generators not current with required governor tests
  Some entities repeatedly fall short of TAC-approved telemetry availability level

## Slide 29: Questions?