## Slide 1: PGRR33: Dynamics Flat Start Cases Preparation
Carol Chessmore
Oncor
2013 DWG Vice Chair
2014 DWG Chair - Pending ROS Approval
January 9, 2014
ERCOT ROS Meeting
Austin, TX

## Slide 2: ROS Approval of PGRR33
Brings Planning Guide consistent with approved procedures
ERCOT Staff prepare Dynamic Flat Start Cases
ROS Approved in July 11, 2013 as part of DWG Procedure Manual Revision 8
Supports ERCOT as the “One Stop Shop” for data collection and study cases
Supports consistency with RARF, SSWG and SPWG data preparation
DWG and PLWG support the Revision

## Slide 3: Proposed PGRR33 Change
DWG Manual Revision 8 - Approved by ROS on July 11, 2013
  After January 1st, 2015, ERCOT shall prepare all the flat start cases
PGRR 33 revision to Planning Guide section 6.2.4
  (1) In order to maintain simulation-ready base cases and associated dynamics data files for use in dynamic simulations, the DWG ERCOT, in consultation with ERCOT the DWG, shall perform dynamic simulations, called flat-start simulations, as described in the Dynamics Working Group Procedure Procedural Manual

## Slide 4: NERC Roles and Definitions
Planning Authority (Planning Coordinator in new standard)
  The responsible entity that coordinates and integrates transmission facility and service plans, resource plans, and protection systems
  ERCOT is the registered Planning Authority (PA)
Resource Planner
  The entity that develops a long-term (generally one year and beyond) plan for the resource adequacy of specific loads (customer demand and energy requirements) within a Planning Authority Area.
  ERCOT is the registered Resource Planner (RP)
Transmission Planner
  The entity that develops a long-term (generally one year and beyond) plan for the reliability (adequacy) of the interconnected bulk electric transmission systems within its portion of the Planning Authority Area.
  TSPs such as Oncor, CNP, AEP , LCRA, etc are registered Transmission Planners (TPs)

## Slide 5: Appropriate Entity for Coordinator
  ERCOT is the Appropriate Entity for the Flat Start Coordinator
    Precedent
      ERCOT inputs Generator data into the SSWG case
      ERCOT has been the DWG Flat Start Coordinator in the past
    ERCOT has Experienced Dynamic staff
      Flat Start Case Building requires advanced skills and knowledge of a wide variety of models both Conventional and Renewable
      Some TSPs do not have Wind generators or other renewables in their area and are unfamiliar with Renewable Generator models
    Improved Data and Process Consistency
      ERCOT is used to looking across the whole system
      ERCOT has access to the Dynamic portion of the RARF. TSPs do not have full access to the Dynamic datasheets attached to the RARF

## Slide 6: Appropriate Entity for Coordinator
  ERCOT is the Appropriate Entity for the Flat Start Coordinator (Continued)
    Improved Communication
      Close the loop between Flat Start Model Adjustments and the RARF Model Submission
      As ERCOT Flat Start Coordinator, ERCOT communicates better with generators since they are more aware of common model issues
      ERCOT has a built-in system (website posting) for distributing large files.
        Outside companies as Flat Start Coordinator have to give the package (100Mb) to ERCOT to post.
        Most TSPs don’t have FTP sites and email file limits may force the Pass Case package to be chopped into pieces.
        FTP site to FTP site communication brings up security and IT issues

## Slide 7: Appropriate Entity for Coordinator
  ERCOT is the Appropriate Entity for the Flat Start Coordinator (Continued)
    Improved Compliance with NERC Standards
      Documented communication between ERCOT, TSPs, and Generators on Dynamic Models
      If ERCOT is the Coordinator, TSPs and Generators receive direct confirmation that data submittal was received by ERCOT
      TSPs and Generators have direct confirmation that ERCOT is aware of tuning that needed to be done on Dynamic models
      ERCOT manages the RARF process so any needed changes shown by the Flat Start process can be followed up by ERCOT directly with the Generator

## Slide 8: Cost Impact to TSPs
TSPs take turns so 3 TSPs for 3 Flat Starts per year
  Oncor, CNP, AEP, LCRA, CPS, Austin Energy, and STEC actively participate in DWG
  However, if one TSP is required to do it, then all TSPs (even non-active DWG members) need to serve a term as coordinator
    Costs quickly balloon under this scenario
Personnel Requirements per TSP
  Each TSP needs to maintain a person who is experienced enough to troubleshoot both inside and outside its Area
  Even if a TSP does not perform a Flat Start that year, the TSP needs to maintain a person with the skill set to perform a DWG Flat Start
  At present, TSPs do not have the long term resources to plan for the resources/budget/schedule needed to perform the flat start case
  May require each TSP to add a Third of a Full Time Employee (FTE)
  Possibility of delays in publishing the case and performing studies
Summary
  Third of FTE per TSP with a Total of 2+ FTE for TSPs

## Slide 9: Cost Impact to TSPs
Impact
  $45k per TSP to support one Flat Start per year
    Assuming the Coordinator is experienced with the ERCOT system and Wind generator models and other renewable models
  $50k per TSP to support one Flat Start
    For Coordinators unfamiliar with ERCOT
    TSPs lacking Wind generators and other renewables in their area,
  Experienced
    $45k * 6 TSPs = $270k per year
    $45k * 4 TSPs = $180k per year
  Inexperienced
    $50k * 6 TSPs = $300k per year
    $50k * 4 TSPs = $200k per year
  As more TSPs begin to participate to take their turn as coordinator, costs escalate above $300k per year
$180k-$300k+ per year for TSPs to support DWG Flat Starts

## Slide 10: Cost Summary
ERCOT as the
Coordinator
TSPs as the
Coordinator
ERCOT needs to maintain one person who is experienced enough to troubleshoot across the ERCOT system
ERCOT Impact Analysis
  Half of an FTE
  $120k-$130k to support 3 Flat Starts per year
Cost savings
  $60k-$170k+ per year
Each TSP needs to maintain a person who is experienced enough to troubleshoot both inside and outside their Area
TSP Impact Analysis
  Third of an FTE per TSP,
  Total 2 FTE for 6 TSPs
  $45k-$50k per TSP per year $180k-$300k+ per year for TSPs to support all 3 Flat Starts

## Slide 11: Conclusion
DWG and PLWG support PGRR 33
ERCOT is the NERC Planning Coordinator and NERC Resource Planner so ERCOT is the Appropriate Entity to be the Flat Start Coordinator
Cost Savings, Improved Efficiency , Reduced Delays from reducing pool of Flat Start Coordinators from 6+ Entities to One Entity
Having a single entity as the Flat Start Coordinator leads to
  Improved Consistency of the Flat Start process and Dynamic models
  Improved Communication between ERCOT, Generators and TSPs
  Improved Compliance with NERC standards

## Slide 12: Appendix
Flat Start Case Building Details

## Slide 13: Need for a Flat Start Dynamics Case
Needed by both ERCOT and TSPs
New and Existing Dynamic Data Submissions are tested in the Dynamics Case.
  Issues can be seen that are not caught earlier since generators are interacting together in the system
A Stable No Disturbance Case with a good initialization is required for both ERCOT and TSPs to perform Dynamic Analysis studies on the transmission system
Dynamic Analysis studies are required by NERC standards and the ERCOT Planning Guide
Dynamic Analysis can lead to projects that help stabilize the Transmission Grid around Generators
  Example: CREZ Reactive Study resulted in SVCs and Reactors
  Example: Parkdale and Renner SVCs in the DFW Area
  Example: ERCOT Panhandle Study
VSAT and TSAT - used by ERCOT Operations
  ERCOT maintains VSAT and TSAT models
  ERCOT uses PSSE models as a basis for VSAT and TSAT models

## Slide 14: NERC Standards Require a Flat Start Case
Standard TPL-001-0.1-System Performance Under Normal Conditions
  B. R1. The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands,
The following standards require a Base Case or Flat Start Dynamic Case (No Contingency case) in order for analysis to be completed.
  Standard TPL-002-0b: Loss of a Single BES Element (Category B)
  Standard TPL-003-0b : Loss of Two or More BES Elements (Category C)
  Standard TPL-004-0a: Extreme BES Events (Category D

## Slide 15: DWG Manual Revision 8 Full Language
Approved by ROS on July 11, 2013
4.1.1 Schedule for Dynamic Data Updates and Flat Start Cases
  Each February, the DWG shall prepare a schedule for updating dynamics data and preparing the DWG flat start cases
  The DWG shall prepare the following flat start cases based on the following SSWG steady state cases:
    Dataset A summer on-peak
    A future year Dataset B summer on-peak case
    The future year Dataset B high wind low load case
  The DWG may choose to flat start additional cases
  After January 1st, 2015, ERCOT shall prepare all the flat start cases

## Slide 16: Flat Start Coordinator History
2010 - Does not include CREZ Reactive Study Flat Starts
  CY2011 – ERCOT Staff
  FY2013 – ERCOT Staff
2011
  CY2011 – ERCOT Staff
  FY2015 – ERCOT Staff
2012
  CY2012 – ERCOT Staff
  FY2017- TSP prepared (AEP)
  2013 - Added HWLL Flat Start requirement
  CY2013 – ERCOT Staff
  HWLL2016 – ERCOT Staff
  FY2018 – TSP prepared (Austin Energy)

## Slide 17: Future Flat Start Schedule
2014
  CY2014 – TSP Prepared (LCRA)
  HWLL2017 – TSP Prepared (AEP)
  FY2019 – TSP Prepared (Oncor)
2015
  CY2015 – TSP Prepared (CNP)
  HWLL2018 – ERCOT Staff (With PGRR33 Approval)
  FY2020 –ERCOT Staff (With PGRR33 Approval)

## Slide 18: What is a Flat Start
Stable No Disturbance Base Case
  A Stable Base Case is indicated by flat lines on time plots since there is no changes that force the generator control systems to respond.
  With a Contingency, a nearby generator would initially oscillate as it responds to the disturbance. Then it would damp down to a new stable steady value
  With poor or inconsistent data, generators oscillate without disturbance or go completely unstable
Unstable Case
Stable Case

## Slide 19: Difference between a Steady State Study and a Dynamics Study
Steady State Study
Dynamic Study
Time is not considered
Uses Simple Generator Model
  Pmax, Pmin, Qmax, Qmin
Does not use fault impedance data
Uses Matrix Math
  No Initialization
  Less sensitive to Parameter Changes
Adds time as a parameter
Adds Generator Component data
  Turbine, Governor, Exciter, Power System Stabilizer, Over Excitation Limiter, etc
Uses Fault Impedance data to model a fault condition
Uses Differential Equations
  Initialization
  Sensitive to Parameter Changes

## Slide 20: Case Creation Flow Chart
Pass Case Posted for Review by DWG and ERCOT
DWG
Conventional
Gen RARF
Models
Renewable
Gen RARF Models
Flat Start Coordinator
TSP
TSP
Final Case Package
Pass Case Package
(100MB)
TSP

## Slide 21: Input Data for Flat Starts
Uses a SSWG seed case
Adds dynamic models for Generator Components
  Turbine, Governor, Exciter, Power System Stabilizer, Over Excitation Limiter, etc
  TSPs do not directly see the PSSE datasheets in the RARF
  ERCOT disseminates generator updates to TSPs
Combined Cycle Dispatch
  adjusted with Historical Dispatch Data using a Python program to match Steam Turbine Governor Models
Adds collector systems for Wind Generators
User Defined Model data is compiled into a form that PSSE can use for simulation

## Slide 22: Labor Costs: Tuning an Unstable Base Case
Each Case has to be individually tuned to that Generation Dispatch, Load Level, and Topology
Process is iterative and time consuming
Because Dynamic Analysis uses a Differential Equation Solution Process, the analysis is sensitive to changes in parameter data
Changes in Generation Dispatch, Zsource, voltage tuning, are made to obtain a Stable No Disturbance Case with a good initialization (no out of limit messages)
If the case does not initialize well, then the simulation stops until the case is tuned to obtain a good initialization. Problems with initialization can be because of missing data or Dynamic Data that does not match Steady State Data
A case that initializes but has errors might have Dispatches that force the generator to its dynamic limit and/or over its dynamic limit. Parameters are adjusted to get a match between the Steady State and Dynamic data