ERCOT Operations Report

December 2013 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 12/2/2013 16:03 | 59.740 | 76 | Unit trip with approximately 840 MW net |
| 12/8/2013 13:07 | 59.894 | 4 | Unit trip with approximately 576 MW net |
| 12/9/2013 8:43 | 59.814 | 71 | Unit trip with approximately 933 MW net |
| 12/13/2013 19:37 | 59.739 | 138 | Two units tripped with approximately 1348 MW net |
| 12/17/2013 11:45 | 59.819 | 52 | Unit trip with approximately 786 MW net |
| 12/30/2013 9:44 | 59.830 | 69 | Unit trip with approximately 785 MW net |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less

than 1 Hz are considered to be inter- area, while higher frequencies indicate local events.  Industry standards

specify that damping ratio for inter-area oscillations should be 3.0% or greater.  All events listed below

indicate the ERCOT system transitioned well after each disturbance.

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 12/2/2013 16:03:48 | Unit Trip | Approx. 178 sec | The event was caused by the loss of one unit. The unit was generating 840 MW net before the trip, the frequency dropped to 59.739 Hz. The oscillating frequency of 0.67 Hz with 6.49% damping ratio was observed. |
| 12/9/2013 08:43:06 | Unit Trip | Approx. 206 sec | The event was caused by the loss of one unit. The unit was generating 933 MW net before the trip, the frequency dropped to 59.813 Hz. The oscillating frequency of 0.625 Hz with 6.5% damping ratio was observed. |
| 12/13/2013 19:37:48 | Unit Trip | Approx. 280 sec | The event was caused by the loss of two units. The units were generating 1348 MW net before the trip, the frequency dropped to 59.737 Hz. The oscillating frequency of 0.66 Hz with 7.25% damping ratio was observed. |
| 12/17/2013 11:45:38 | Unit Trip | Approx. 204 sec | The event was caused by the loss of one unit. The unit was generating 786 MW net before the trip, the frequency dropped to 59.816 Hz. The oscillating frequency of 0.67 Hz with 9.4% damping ratio was observed. |
| 12/30/2014 09:44:18 | Unit Trip | Approx. 342 sec | The event was caused by the loss of one unit. The unit was generating 785 MW net before the trip, the frequency dropped to 59.828 Hz. The oscillating frequency of 0.65 Hz with 14.74% damping ratio was observed. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 12/2/13 16:04:06 | 12/2/13 16:08:02 | 0:03:56 | 1317.7 |  |
| 12/8/13 13:07:40 | 12/8/13 13:11:08 | 0:03:28 | 278.64 |  |
| 12/9/13 8:43:24 | 12/9/13 8:47:52 | 0:04:28 | 693.28 |  |
| 12/13/13 19:38:06 | 12/13/13 19:43:54 | 0:05:48 | 1209.5 |  |
| 12/17/13 11:45:54 | 12/17/13 11:50:30 | 0:04:36 | 760.83 |  |
| 12/30/13 9:44:33 | 12/30/13 9:49:38 | 0:05:05 | 610.39 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages

| Contingency Description | Overloaded Element | # Days Active |
| --- | --- | --- |
| Techridge - Aen Dunlap 138 kV | Dunlap - Decker 138 kV | 15 |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 13 |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney Tnp 138 kV | 11 |
| DCKT Austrop - Garfield Aen and Zorn 345 kV | Dunlap - Decker 138 kV | 8 |
| Loyola Sub - Kleberg Aep 138 kV | Loyola Sub 138_69_1 138/69kV | 8 |
| Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 8 |
| DCKT Tonkawa Switch - Scurry County South Switch 345 kV | Bluff Creek Switch - Exxon Sharon Ridge 138 kV | 7 |
| Koch Up River - Gila 138 kV | Gila - Hiway 9 138 kV (GILA_HIWAY_2) | 7 |
| North Edinburg - Lon Hill 345 kV | Las Pulgas - Raymondville 2 138 kV | 7 |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 7 |
| DCKT Paris Switch - Valley Ses and Valley South 345 kV | Brookstone Tap - Bonham Lake Poi 138 kV | 5 |
| DCKT Rio Hondo - North Edinburg 345 kV and Harlingen Switch 138 kV | Rio Hondo - Burns Sub 138 kV | 5 |
| DCKT Paris Switch - Valley Ses and Valley South 345 kV | Paris Switch AXFMR1 (3) 345/138 kV | 4 |
| Laquinta - Lobo 138 kV | Falfurrias 138_69A1 138/69 kV | 4 |
| DCKT Odessa Ehv Switch - Quail Switch - Longshore Switch 345 kV | Stanton East - 1276_Triangle 138 kV | 3 |
| DCKT Sam Switch - Tradinghouse Ses 345 kV | Whitney AXFMR2 (3) 345/138 kV | 3 |
| DCKT Singleton - Zenith 345 kV | Tomball - Louetta 138 kV | 3 |
| Oxychem Ingleside - Ingleside Cogen Switch 138 kV (Icosw_Idpsw_2B) | Dupont Pp1-Ingleside - Dupont Switch-Ingleside 138 kV (I_DUPP_I_DUPS1) | 3 |
| Victoria - Coleto Creek 138 kV (Coleto_Victor1) | Victoria - Coleto Creek 138 kV (Coleto_Victor2) | 3 |
| Lytton Springs LY_AT2 345/138 kV | Lytton Springs LY_AT1 345/138 kV | 3 |
| Basecase | Langford Wind Power Llc - Santiago 138 kV | 2 |
| Basecase | Ena Snyder Wind - Wkn_Bkr 69 kV | 2 |
| DCKT Krum West Switch - Lewisville Switch - Roanoke Switch 345 kV | Teasley Substation - Pockrus Substation 138 kV | 2 |
| DCKT Tomball - Singleton 345 kV | Zenith - Th Wharton 345 kV (Thwzen71) | 2 |
| Alice - Kingsville 138 kV | Lon Hill - Robstown Tap 69 kV | 2 |
| North Edinburg - Lon Hill 345 kV | Celanese Bishop - Kleberg Aep 138 kV | 2 |
| Desoto Switch - Ennis Switch 138 kV | Ennis West Switch - Waxahachie 138 kV | 2 |
| Rio Hondo - North Edinburg | Weslaco Switch - Weslaco Sub 138 kV | 2 |
| Aspermont Aep - Spur 138KV | Wolfgang - Rotan 69 kV | 2 |
| Stanton East AXFMRH 138/69 kV | Stanton East - Big Spring West 138 kV | 2 |
| Basecase | SOP110 | 1 |
| Basecase | West to North | 1 |
| DCKT Carrolton Northwest - Lewisville Switch 345 kV | Lakepointe Tnp - Carrollton Northwest 138 kV | 1 |
| DCKT Pilot Knob - Onion Creek and Hicross Aen - Garfield Aen 138 kV | Advanced Micro Devices Aen - Pedernales 138 kV | 1 |
| DCKT Tonkawa Switch - Scurry County South Switch 345 kV | Bluff Creek Switch - Exxon Sharon Ridge 138 kV | 1 |
| DCKT Singleton - Zenith 345 kV | Hockley - Betka 138 kV | 1 |
| DCKT Singleton - Zenith 345 kV | Tomball - Rothwood 138 kV | 1 |
| DCKT Trinidad Ses - Tri Corner and Watermill Switch 345 kV | Trinidad Ses AXFMR6 (3) 345/138 kV | 1 |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Rincon - Airco Aep 138kV | 1 |
| DCKT West Levee Switch - 800/900 Network 138 kV | East Levee Switch - Reagan Street 138 kV (3410_A) | 1 |
| Vanderbilt Switching Station - El Toro Switching Station 69 kV | Sam Rayburn Switching Station 138_69_2 138/69 kV | 1 |
| Falcon Seaboard - Midland East 345 kV | Stanton East - 1276_Triangle 138 kV | 1 |
| Fort Stockton Plant - Barrilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 1 |
| Laquinta - Lobo 138 kV | Falfurrias - Premont 69 kV | 1 |
| North Edinburg - Lon Hill 345 kV | Kleberg Aep - Loyola Sub 138 kV | 1 |
| North Edinburg - Lon Hill 345 kV | Las Pulgas - Rio Hondo 138 kV | 1 |
| North Edinburg - Lon Hill 345 kV | Lon Hill - Robstown Tap 69 kV | 1 |
| Richland Chambers - Trinidad Ses 345 kV (Line 21) | Richland Chambers - Trinidad Ses 345 kV (Line 31) | 1 |
| Stadium Aep - Alice 69 kV | Lon Hill - Robstown Tap 69 kV | 1 |
| Tonkawa Switch - Scurry County South Switch 345 kV (34520) | Bluff Creek Switch - Exxon Sharon Ridge 138 kV | 1 |
| West Conoco Load - Escondido and Asherton 138 kV | Brackettville - Hamilton Road 138 kV | 1 |
| Schulenburg - Weimar - Glidden Lcra 138 kV | Victoria - Magruder 138 kV (Magrud_Victor2) | 1 |
| Zenith - Th Wharton 345 kV (Thwzen98) | Zenith - Th Wharton 345 kV (Thwzen71) | 1 |
| Decker Unit 2 | Dunlap - Decker 138 kV | 1 |
| Dunlap AT1H 345/138 kV | Austrop - Dunlap 345 kV | 1 |
| Midland East AXFMR1 (3) 345/138 kV | Stanton East - 1276_Triangle 138 kV | 1 |
| Victoria 138_69_A2 138/69 kV | Victoria - Magruder 138 kV (Magrud_Victor2) | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 1 |
| SOP110 | 1 |

Congestion Cost

Binding Constraints – Year to Date

| Contingency | Binding Element | Number of 5-min intervals | Shadow Price Range $/MWh | Estimated Congestion Rent $ (Shadow Price*Limit) | Transmission Project |
| --- | --- | --- | --- | --- | --- |
| Midland East to Odessa EHV 345 kV & Moss Switch 345/138 kV Xfmr | Odessa - Odessa North 138 kV | 9038 | 0 - 3500 | 57,143,394 | 13TPIT0136, 14TPIT0054 |
| Midland East to Odessa EHV 345 kV & Moss Switch 345/138 kV Xfmr | Odessa EHV Switch - Big Three Odessa Tap 138kV | 4335 | 0 - 3500 | 31,785,167 | 13TPIT0153 |
| Roanoke Switch - West Denton 345 kV & Roanoke Switch - Lewisville Switch 345 kV; or West Denton - Roanoke Switch 345 kV; or West Denton - Rdwells 138 kV | Jim Cristal - North Denton 138kV | 1407 | 0 - 3500 | 18,679,874 | 14TPIT0047 |
| DCKT Roansprairie - Kuykendahl - King & Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 473 | 0 - 4500 | 17,737,088 |  |
| Sun Switch - Golden Switch 138 kV; Sun Switch - Morgan Creek SES 138 kV | Bluff Creek Switch - China Grove Switch 138 kV | 1042 | 0 - 3500 | 17,681,085 | 12TPIT0058, 13TPIT0098 |
| Roanoke Switch - West Denton 345 kV & Roanoke Switch - Lewisville Switch 345 kV; or West Denton - Roanoke Switch 345 kV | Fort Worth - Teasley 138 kV | 2813 | 0 - 3500 | 16,898,845 | 14TPIT0047 |
| Amoco South Foster to Westover 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1204 | 0 - 3500 | 15,801,329 | 13TPIT0098, 13TPIT0093 |
| Morgan Creek SES 345/138 kV Autotransformer 2 | Morgan Creek SES 345/138 kV Autotransformer 4 | 394 | 0 - 4500 | 13,917,840 |  |
| Morgan Creek SES AXFMR2 345/138kV | Mogan Creek SES AXFMR1 345/138kV | 4841 | 0 - 1370 | 12,209,796 |  |
| Austrop 345/138 kV Xfmr & Garfield LCRA 345/138 kV Xfmr | Austrop 345/138 kV Xfmr | 1965 | 0 - 4500 | 11,898,409 | 10TPIT0031 |
| West Denton - Rdwells 138 kV | Teasley - Pockrus Substation 138 kV | 1203 | 0 - 3500 | 11,278,354 | 5YTP [2012-R46] |
| Cangon AXFMR3 345/138kV | Cangon AXFMR4 345/138kV | 3515 | 0 - 3500 | 10,671,747 |  |
| DCKT Roansprairie - Kuykendahl - King & Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 3029 | 0 - 4500 | 9,828,893 |  |
| McNeil - Gilleand Creek 138 kV | Hutto - Round Rock NE 138 kV | 1983 | 0 - 3500 | 7,822,046 |  |
| Ajo - Rio Hondo 345 kV | North Edinburg - Lon Hill 345 kV | 39 | 2 - 4500 | 7,633,932 | 14TPIT0050 |
| Calallen Sub to Lon Hill 69kV | Lon Hill - Robstown Tap 69kV | 781 | 0 - 2800 | 7,270,688 | 13TPIT0220 |
| DCKT Salado Switch - Killeen Switch 345kV | Temple Switch - Temple Southeast 138kV | 716 | 0 - 3500 | 6,980,592 | 5YTP[2012-R45] |
| Garfield LCRA 345/138 kV Xfmr & Austrop - Daffin 138 kV | Austrop - Dunlap 138 kV | 836 | 0 - 3500 | 6,752,664 | 10TPIT0031 |
| Odlaw Switchyard to Uvalde AEP 138kV | Hamilton Road - Maverick 138kV | 5716 | 0 - 2905 | 6,469,174 | 16TPIT0024 |
| Wink 138/69 kV Autotransformer; or Wink - Wink Sub 138 kV | Wink Basin Tap - Wink Sub 69 kV | 772 | 0 - 2800 | 6,378,270 | 17TPIT0018, 5YTP[2012-R4] |

Binding Constraints – December 2013

| Contingency | Binding Element | Number of 5-min intervals | Shadow Price Range $/MWh | Estimated Congestion Rent $ (Shadow Price*Limit) | Transmission Project | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| DCKT Austrop - Garfield LCRA& Zorn 345kV and Techridge - AEN Dunlap 138kV | Decker - AEN Dunlap 138kV | 2415 | 0 - 3500 | 4,207,636 | 16TPIT0036, 10TPIT0031, 07TPIT0050 | Planned outage of McNeil - Decker 138 kV |
| North Edinburg - Rio Hondo 345kV | Weslaco Switch - Weslaco Sub 138kV | 193 | 0 - 3500 | 3,574,773 | 11TPIT0002 14TPIT0050 14TPIT0051 | Planned outage of Ajo - Nelson Sharpe 345 kV |
| Koch Up River - Gila 138kV | Gila - Hiway_9 138kV | 1338 | 0 - 3500 | 3,197,365 |  | Forced outage of Gila - Hiway 9 (GILA_HIWAY_1) 138KV |
| Orange Grove Switching Station - Lon_hill 138kV | Lon_hill - Smith 69kV | 766 | 0 - 2800 | 1,068,146 | 2012-R18 | High load in Corpus Christi area |
| Laquinta - Lobo 138kV | Bruni Sub 138_69_1 138/69kV | 1250 | 0 - 2800 | 1,000,282 |  | High area wind |
| North Edinburg - Lon_hill 345kV | Las Pulgas - Raymondville 2 138kV | 847 | 0 - 2135 | 965,923 | 11TPIT0002, 14TPIT0050, 14TPIT0051 | Planned outage of Ajo - Nelson Sharpe 345 kV |
| DCKT Odessa EHV Switch - Longshore Switch & Quail Switch 345kV and Midland East AXFMR1 345/138kV | Stanton East - 1276 Triangle 138kV | 410 | 0 - 1537 | 890,008 | 14TPIT0052 | High area wind |
| Lytton Springs LY_AT2 345/138kV | Lytton Springs LY_AT1 345/138kV | 269 | 0 - 4500 | 808,271 |  | Planned outage of Wyldwood - Wolf Lane 138 kV |
| North Edinburg - Lon_hill 345kV and Alice to Stadium AEP 69kV and Alice to Kingsville 138kV | Lon_hill - Robstown Tap 69kV | 114 | 0 - 2800 | 802,397 | 12TPIT0180 | Planned outage of Callen Sub - Lon Hill 69 kV |
| DCKT Paris Swith - Valley SES & Valley South 345kV | Paris Switch AXFMR1 345/138kV | 342 | 0 - 2360 | 599,206 |  | Forced outage of Monticello Ses - Allen Switch 345 kV |
| DCKT Riohondo - North Edinburg 345kV and Harlingen Switch 138kV | Burns Sub - Riohondo 138kV | 610 | 0 - 1507 | 528,208 | 11TPIT0002, 14TPIT0050, 14TPIT0051 | Planned outage of Ajo - Nelson Sharpe 345 kV |
| DCKT West Levee Switch - 800/900 Network 138kV | East Levee Switch - Reagon Street 138kV | 61 | 0 - 3500 | 511,875 |  | Planned outage of West Network - East Levee Switch 138 kV DCKT |
| DCKT Scurry County South Switch - Tonkawa Switch 345kV | Bluff Creek Switch - Exxon Sharon Ridge 138kV | 588 | 0 - 109 | 387,331 | 12TPIT0058 | High West-North flow due to high West wind output |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Airco AEP - Rincon 138kV | 91 | 0 - 3500 | 301,834 | 08TPIT0132 08TPIT0131 | High output from Corpus Christi area |
| DCKT Paris Swith - Valley SES & Valley South 345kV | Brookstone Tap - Bonhan Lake POI 138kV | 543 | 0 - 138 | 297,175 |  | Forced outage of Monticello Ses - Allen Switch 345 kV |
| Laquinta - Lobo 138kV | Falfur 138_69A1 138/69kV | 259 | 0 - 632 | 194,682 |  | Multiple planned area outages |
| North Edinburg - Lon_hill 345kV | Celanese Bishop- Kleberg AEP 138kV | 60 | 0 - 470 | 189,568 | 11TPIT0002, 14TPIT0050, 14TPIT0051 | Planned outage of Ajo - Nelson Sharpe 345 kV |
| Oxychem Ingleside - Ingleside Cogen Switch 138kV | Dupont PP1 Ingleside - Dupont Switch - Ingleside 138kV | 618 | 0 - 3500 | 167,174 |  | Planned outage of Ingleside Cogen Switch - Dupont Switch-Ingleside 138 kV |
| Coleto Creek - Victoria 138kV (COLETO_VICTOR1) | Coleto Creek - Victoria 138kV (COLETO_VICTOR2) | 431 | 0 - 260 | 161,590 |  | High area generation |
| DCKT Singleton - Tomball 345kV | Th Wharton - Zenith 345 kV | 229 | 0 - 47 | 119,876 |  | Planned outage of Th Wharton - Zenith 345 kV (THWZEN98A) |

Wind Generation as a Percent of Load

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Power Operations Bulletin 648 - DC Tie Desk V1 Rev23 Power Operations Bulletin 649 - Real Time Desk V1 Rev27 Power Operations Bulletin 650 - Reliability Unit Commitment Desk V1 Rev22 Power Operations Bulletin 651 - Resource Desk V1 Rev26 Power Operations Bulletin 652 - Shift Supervisor Desk V1 Rev24 Power Operations Bulletin 653 - Transmission and Security Desk V1 Rev28 |  |  |
| --- | --- | --- |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

12/09 19:05	ERCOT issued an Advisory due to the Voltage Security Assessment Tool (VSAT) not solved for 30 minutes.

12/12 06:30	ERCOT issued an Advisory due to the Voltage Security Assessment Tool (VSAT) not solved for 30 minutes.

Communication Issues

None

## ERCOT peak (Unofficial)

12/10 08:00 53,690 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 | 2.83 |
| March | 2.24 | 2.02 | 3.49 | 2.68 |
| April | 2.47 | 3.55 | 2.78 | 2.81 |
| May | 2.63 | 3.27 | 3.09 | 3.12 |
| June | 2.84 | 2.28 | 2.85 | 2.51 |
| July | 2.39 | 1.63 | 2.85 | 2.70 |
| August | 2.29 | 2.28 | 2.96 | 2.07 |
| September | 3.14 | 2.70 | 3.43 | 2.41 |
| October | 2.37 | 3.51 | 2.99 | 2.87 |
| November | 3.46 | 3.38 | 2.90 | 3.48 |
| December | 2.60 | 2.99 | 3.47 | 3.37 |
| Annual Average | 2.83 | 2.83 | 3.02 | 2.86 |

OCN, Advisory, Watch & Emergency Notices

Capacity

OCN

None

Advisory

| Date | Event |
| --- | --- |
| 12/5/2013 06:00 | ERCOT issued an Advisory due to forecasted freezing rain and sleet with one half inch of ice accumulation in the West, North, and North Central Regions. |
| 12/9/2013 19:05 | ERCOT issued an Advisory due to the Voltage Security Assessment Tool (VSAT) not solved in the last 30 minutes. |
| 12/12/2013 06:30 | ERCOT issued an Advisory due to the Voltage Security Assessment Tool (VSAT) not solved in the last 30 minutes. |

Transmission Watch

None

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None