## One Area
Freq (hz) | 60
Load (MW) | 360
GENERATOR #1
Gen (MW) | 80
Setpt (MW) | 80 | 0 | 60.3 | 60.3 | 60.3 | 60
Rating (MW) | 300 | 65 | 60.3 | 60.3 | 60.3 | 60
Droop (%) | 10% | 80 | 60 | 60.3 | 60.3 | 60
Gov (MW/hz) | 50 | 95 | 59.7 | 60.3 | 60.3 | 60
GENERATOR #2 |  | 90 | 59.7 | 60.3 | 60.3 | 60
Gen (MW) | 120 | 120 | 59.7 | 60 | 60.3 | 60
Setpt (MW) | 120 | 150 | 59.7 | 59.7 | 60.3 | 60
Rating (MW) | 450 | 100 | 59.7 | 59.7 | 60.3 | 60
Droop (%) | 7.5% | 160 | 59.7 | 59.7 | 60 | 60
Gov (MW/hz) | 100 | 220 | 59.7 | 59.7 | 59.7 | 60
GENERATOR #3 |  | 300 | 59.7 | 59.7 | 59.7 | 60
Gen (MW) | 160 | Freq w1&2 | 59.94 | 59.94
Setpt (MW) | 160 | G#1 | 83
Rating (MW) | 600 | G#2 | 126
Droop (%) | 5% | G#3 | 160
Gov (MW/hz) | 200 | Total | 369

## LFC
Freq (hz) | 60
Load (MW) | 360
GENERATOR #1
Gen (MW) | 80
Setpt (MW) | 80 | 0 | 60.3 | 60.3 | 60.3 | 60
Rating (MW) | 300 | 65 | 60.3 | 60.3 | 60.3 | 60
Droop (%) | 10% | 80 | 60 | 60.3 | 60.3 | 60
Gov (MW/hz) | 50 | 95 | 59.7 | 60.3 | 60.3 | 60
GENERATOR #2 |  | 90 | 59.7 | 60.3 | 60.3 | 60
Gen (MW) | 120 | 120 | 59.7 | 60 | 60.3 | 60
Setpt (MW) | 120 | 150 | 59.7 | 59.7 | 60.3 | 60
Rating (MW) | 450 | 100 | 59.7 | 59.7 | 60.3 | 60
Droop (%) | 7.5% | 160 | 59.7 | 59.7 | 60 | 60
Gov (MW/hz) | 100 | 220 | 59.7 | 59.7 | 59.7 | 60
GENERATOR #3 |  | 300 | 59.7 | 59.7 | 59.7 | 60
Gen (MW) | 160 | Freq w1&2 | 59.94 | 59.94 | 60.3 | 59.7
Setpt (MW) | 160 | G#1 | 83 |  | 65 | 95
Rating (MW) | 600 | G#2 | 126 |  | 90 | 150
Droop (%) | 5% | G#3 | 160 |  | 100 | 220
Gov (MW/hz) | 200 | Total | 369 |  | 255 | 465
[5 empty] | 60 | 60
[5 empty] | 255 | 465

## CNI
| AREA A | AREA B | SYSTEM
Gen (MW) | 200 | 160 | 360
Load (MW) | 200 | 160 | 360
Interch (MW) | 0 | 0
Sch Int (MW) | 0 | 0
Int Dev (MW) | 0 | 0
Freq Dev(hz) |  |  | 0
Set Pt (MW) | 200 | 160 | 360
Freq (hz) | AREA A | Scheduled | AREA B | 0 | 60.3 | 60.3 | 60.3 | 60
60 | Load (mw) | AtoB (mw) | Load (mw) | 65 | 60.3 | 60.3 | 60.3 | 60
Sch Freq(hz) | 200 | 0 | 160 | 80 | 60 | 60.3 | 60.3 | 60
60 | GEN #1 | GEN #2 | GEN #3 | 95 | 59.7 | 60.3 | 60.3 | 60
Setpt (MW) | 80 | 120 | 160 | 90 | 59.7 | 60.3 | 60.3 | 60
Gen (MW) | 80 | 120 | 160 | 120 | 59.7 | 60 | 60.3 | 60
Rating (MW) | 300 | 450 | 600 | 150 | 59.7 | 59.7 | 60.3 | 60
Droop (%) | 10% | 7.5% | 5% | 100 | 59.7 | 59.7 | 60.3 | 60
Gov (MW/hz) | 50 | 100 | 200 | 160 | 59.7 | 59.7 | 60 | 60
|  |  |  | 220 | 59.7 | 59.7 | 59.7 | 60
|  |  |  | 400 | 59.7 | 59.7 | 59.7 | 60

## TLB
| AREA A | AREA B | SYSTEM
Gen (MW) | 200 | 160 | 360
Load (MW) | 200 | 160 | 360
Interch (MW) | 0 | 0
Sch Int (MW) | 0 | 0
B(MW/0.1hz) | 15 | 20 | 35
ACE (MW) | 0 | 0 | 0
FrqBias(MW) | 0 | 0 | 0
Int Dev (MW) | 0 | 0 | 0
Set Pt (MW) | 200 | 160 | 360
Freq (hz) | AREA A | Scheduled | AREA B | 0 | 60.3 | 60.3 | 60.3 | 60
60 | Load(MW) | AtoB(MW) | Load(MW) | 65 | 60.3 | 60.3 | 60.3 | 60
Sch Freq(hz) | 200 | 0 | 160 | 80 | 60 | 60.3 | 60.3 | 60
60 | GEN #1 | GEN #2 | GEN #3 | 95 | 59.7 | 60.3 | 60.3 | 60
Setpt (MW) | 80 | 120 | 160 | 90 | 59.7 | 60.3 | 60.3 | 60
Gen (MW) | 80 | 120 | 160 | 120 | 59.7 | 60 | 60.3 | 60
Rating (MW) | 300 | 450 | 600 | 150 | 59.7 | 59.7 | 60.3 | 60
Droop (%) | 10% | 7.5% | 5% | 100 | 59.7 | 59.7 | 60.3 | 60
Gov (MW/hz) | 50 | 100 | 200 | 160 | 59.7 | 59.7 | 60 | 60
|  |  |  | 220 | 59.7 | 59.7 | 59.7 | 60
|  |  |  | 400 | 59.7 | 59.7 | 59.7 | 60

## Forms of ACE
Forms of the ACE Equation
Interchange Control Form
ACE = NetActInt – Biased NetSchedInt (at Fa)
ACE = NAI – [NSI (at 60Hz) - B*(Fa-Fs)]
Interchange and Frequency Control Form
ACE = [NAI – NSI] + B*(Fa-Fs)
ACE = IntDev + B*FreqDev
Generation Control Form
Since, NAI = NetActGen(NAG) – ContAreaLoad(CAL)
ACE = NAG – CAL – [NSI (at 60Hz) - B*(Fa-Fs)]
ACE = NAG – [CAL + NSI (at 60Hz) - B*(Fa-Fs)]
Define, NetSchedGen (at 60Hz) = CAL + NSI (at 60Hz)
ACE = NAG – [NSG (at 60Hz) - B*(Fa-Fs)]

## Definitions
ACE=Area Control Area (MW)
NAI=NetActInt=Net Actual Interchange
=Sum[area Tie Line Flows] (MW)
NSI=NetSchedInt=Net Scheduled Interchange (MW)
IntDev=Interchange Deviation=NAI-NSI (MW)
FreqDev=Frequency Deviation (HZ)=Fa-Fs
=Actual Frequency-Scheduled Frequency
R=slope of a unit governor steady state speed characteristic curve (negative HZ/MW)
Beta*FreqDev=(1/R)*FreqDev
=governor response of a unit (MW)
FreqBias=B*FreqDev=Sum[1/R]*FreqDev=governor response of an area or a portfolio of units (MW)

## GEN
| AREA A | AREA B | SYSTEM
Gen (MW) | 200 | 160 | 360
Load (MW) | 200 | 160 | 360
Interch (MW) | 0 | 0
Sch Int (MW) | 0 | 0
B(MW/0.1hz) | 15 | 20 | 35
SCE (MW) | 0 | 0 | 0
FrqBias(MW) | 0 | 0 | 0
SchGen(MW) | 200 | 160 | 360
Set Pt (MW) | 200 | 160 | 360
Freq (hz) | AREA A | Scheduled | AREA B | 0 | 60.3 | 60.3 | 60.3 | 60
60 | Load(MW) | AtoB(MW) | Load(MW) | 65 | 60.3 | 60.3 | 60.3 | 60
Sch Freq(hz) | 200 | 0 | 160 | 80 | 60 | 60.3 | 60.3 | 60
60 | GEN #1 | GEN #2 | GEN #3 | 95 | 59.7 | 60.3 | 60.3 | 60
Setpt (MW) | 80 | 120 | 160 | 90 | 59.7 | 60.3 | 60.3 | 60
Gen (MW) | 80 | 120 | 160 | 120 | 59.7 | 60 | 60.3 | 60
Rating (MW) | 300 | 450 | 600 | 150 | 59.7 | 59.7 | 60.3 | 60
Droop (%) | 10% | 7.5% | 5% | 100 | 59.7 | 59.7 | 60.3 | 60
Gov(MW/hz) | 50 | 100 | 200 | 160 | 59.7 | 59.7 | 60 | 60
|  |  |  | 220 | 59.7 | 59.7 | 59.7 | 60
|  |  |  | 400 | 59.7 | 59.7 | 59.7 | 60